## Change Sheet
XPC Detailed Price Sheet Change Log
2025-11-01 | Added SPDU, Added 5YR warranty plans to P91 5-10K, Updated XPD-IT60A, X90-BCBAT price increase
2025-10-01 | Added Li90, J90, X90-1S, Corrected T91-3000 description, Added line cord to XPD-IT15A and XPD-P91A10, Added M90S-RMK, Added X90-2S140K bundles, Price change on SNMP-2PG1
2024-07-26 | Added M90S-12S Modular Single Phase, Corrected Pricing errors
2024-07-11 | Global Price Changes, updated to reflect additions and deletions in 08012024 Price Book, Add M90C.
2023-03-10 | Lowered Prices on V80Li and E91, upgraded E91 battery chargers, Added M90-CBL to M90-BC battery cabinet options , Corrected depth on P91 5-10 bundles, capacity on X902S-70k16B, price on SNMP for X90, price on M90-BOS-06B
2023-01-27 | Added X902S models, Added J60C and J60Ci models, Added California Engineering Stamp to M90-SEIS description
2022-11-17 | Removed TAA Compliant from V80 standard battery models, Correct Price on S70-1000, Add E91 30/40, P90-FRMB changed to up to 2k on P91, removed third party battery packs, Increase price of XPD-IT60A
2022-06-22 | Added E91, Updated pricing on M90 and M90U Models. Updated pricing on M90S SVCADD
2022-04-19 | Increase Price of V80 and P91(g) Lithium Models
2022-04-13 | Change price on SNMP-2PV3, Correct price of XPC-2POSTL, Correct C&C Bypass part numbers and versions offered, Updated T9VCNFG description
2022-03-28 | Corrected Price of S70 models, Added E90 with internal batteries, Updated battery pricing
2022-03-03 | Changed External MBS Part Numbers from 90888 Series to 90885 Series, Changed E90 warranty to 1 Year
2022-02-08 | Updated E90 Prices and Descriptions, Corrected TX91 Battery Pack Prices
2022-01-20 | Corrected Price of M90-ENC80 and M9080-40K08, Corrected Warranty on J60
2022-01-05 | Correct Price on M90-80BATT on ALL and M90U80 and M90U140 Tabs
2022-01-01 | Global Price Increase, Corrected price on M90SU7242, Corrected Part Number for SNMP-2P3, added new old stock to E90
2021-11-03 | Changed M90-BC Breaker to 100A
2021-11-02 | Added Startup and One Year On-site Service option on all M90 and M90U models
2021-09-30 | Global Price Adjustments, Correct pricing on M90-BC bundles with the M90L and M90LU
2021-09-01 | Add M90U, M90LU, M90U-80, and M90U-140, Increase M90, M90L, M90-80, and M90-140 battery and service prices, eChange Part Number on J40SP, Corrected warranty description on T91, corrected PN of MBS
2021-06-22 | Corrected description on P91c-1000 and P91gc-1000, corrected price on P90-BP48 and P90-BP72
2021-06-10 | Price change on J60(i)-350, P80-800 to 1500, P90-BPxx, P80-BP72X, T91-BPxxx, BPXRxU240A, XPD-IT60A, M90S-ENCx, M90S-BC7, removed bundles P80-1100B1 and P80-1500B1, Corrected rating of A60-850
2021-05-26 | Added A60 Series, Change price of M90 C&C Battery Packs to Call For Price
2021-05-24 | Added P91 1.5-3K LI Series, Added V80, V80XR, V80HT, V80 LI Series, Price change on Basic PDUs, removed P90-1000, 1500, 2000, 3000.
2021-04-09 | Corrected M9080 and M90140 pricing on ALL Tab
2021-04-07 | Added P91 and P91g 1-3kVA Lead Acid Series
2021-04-01 | Lower Price on M9080 and M90140, Add TX91 Cords, Change PN and Prices of External Maintenance Bypass Options
2021-03-01 | Global Update to Format, Corrected description of TX91, and receptacles on Surge PDU XPDS1020HV , Added M90-BTS and battery trays to to M90, M90-80, M90-140, removed end of life products
2020-06-24 | Corrected BOM on P91-5KTB2 bundle
2020-06-11 | Lowered price on M90-80, M90-140. M90-BC
2020-06-03 | Corrected TX91 Configurable Output Quantities and add L5-15R
2020-05-22 | Updated Price on J40SP, Added External Bypass Options to TX91 and M90S, Deleted T90-EBP9x0 Battery Packs, Deleted M90 Internal Bbattery Options 3.4 minutes and less
2020-05-06 | Added PowerLOK PDUs, Corrected Capacity of J60(i)-600, Corrected Bundles with XPD-IT15A
2020-05-01 | Added J60-600, 60 Accessories, and JX-200, Corrected price on P80g-5KTB, P80g-3KTB, and M90S-6S24K4, Corrected BOM on P91-10KTB2 and P91-6KTB2, Added M90L Bundles
2020-05-01 | Added TAA Compliant to relative products, Lowered Price of M90S 2-slot and 4-slot
2020-01-22 | Added P91-5KTB2, P91-6KTB2, and P91-10KTB2 Bundles
2020-01-21 | Added M90-80K and M90-140K, Added TX91-CHG external battery charger, Added XPD-IT6KW, Replace XPD-AT15A with XPD-IT15A , Removed XPRT-6BAT, XPRT-10BAT, and XBAT-7.2AH
2019-10-30 | Added TXVR Voltage Regulators
2019-10-22 | Increased price of TX90 6&10kVA, T90-EBP920, 940, and 960 Battery packs.
2019-09-12 | Corrected P91-10kB price and description, Removed TX90i-3000, TX90-2000, TX90-3000, Changed Price on TX91, TX91L
2019-09-11 | Added TX91 and TX91L 3.8-10K, Removed 2U battery from R91, changed price on SPD-0215 ans SPD-815
2019-09-10 | Updated E90 Prices
2019-08-20 | Added SNMP-2PV3 Removed SNMP-2PV2
2019-07-19 | Added P91 5-10kVA
2019-07-01 | Global Price Increases on most UPS Systems, Matching Battery, PDUs. Added M90S
2019-04-19 | Re-design on XPD-AT15A - Do not quote until further notice
2019-04-15 | Delete XPC-515P-18RA, Add XPC-515P-3RA
2019-03-21 | Correct Kaic and Dims on 90881-C208365EC25002MB
2019-03-21 | Removed References to SNMP-1PMINI
2019-03-11 | Changed P90-HT warranty to 3 yrs. Deleted R91-2U battery pack.
2019-03-04 | Corrected P80/P90 5yr service plan description, and P905SP15 price
2019-02-21 | Modified J60 worldwide warranty description
2019-02-18 | Changed M90 service descriptions to include M90S.
2019-01-07 | Changed price of T915SPBP to $320.
2018-12-28 | Changed E90 runtimes. Deleted R90 product.
2018-12-28 | Changed P90g-3KTB price from $2,629 to $2,624, and revised price of 3ph 30 & 40KVA transformer/bypass cabinets.
12/20/2018 Changed 90843 description to include (Eaton Series C) breakers
2018-12-17 | Added E90 Relay card pricing
2018-12-06 | Corrected XPD1415HV price
2018-11-26 | Corrected battery string number on E90-10K3
2018-11-16 | Corrected price of 90843-C208322EC15002E1BK on 3-phase price sheet. Added XBDM-30 to P80 price sheet
2018-11-14 | Changed M90-IT60LW and M90-AT60KW description to reflect that they can be used for input only.
2018-11-09 | Corrected SNMP-1P3Pin pricing and added SNMP-2P3Pin to E90 price sheet
2018-10-02 | Corrected pricing on P90SP15, P90-BP72, XPC-C14-615R, XPDU1415HV
2018-10-23 | Updated service pricing and battery pricing.
2118-10-11 | Fixed ISO6MB Description
2018-10-10 | Updated description of P90-FRMB to include P80-2KVA
2018-10-09 | Updated hardware on all sheets to reflect Nov 1st price increase. Service pricing change to come shortly.
2018-10-05 | Updated M90L battery pack pricing.
2018-10-02 | Corrected kAIC rating on 90885 switches on M90 Price Sheet.
2018-09-05 | Added E90 Pricing.
2018-07-26 | Updated J60 Warranty description
2018-07-24 | Deleted C60 from Detailed Price Sheet
2018-07-17 | Changed price of P90-HT bundles and battery packs.
2018-07-10 | Changed P90-BP48 description to add P80-1500 and P80-2000.
2018-07-09 | Adjusted receptacle numbers and price on SPD-0215, 0815, deleted SPD-1615.
2018-06-29 | Added small footprint torroidal transformer options to M90 price sheet.
6/20/2018 Updated J60 Warranty
2108-06-18 | Revised dims on M90L chassis and description on M90 and M90L chassis
2018-06-06 | Changed price of SNMP-1PMini. Changed label of Dbl Conv 1-3K tab to reflect 1-5K.
2018-05-30 | Replaced SNMP-2PMini with SNMP-2Pv2, and SNMP-EMD with SNMP-EMPv2
2018-05-21 | Corrected V80-2000 line cord description
2018-05-10 | Corrected price of P90L-6KTB4
2018-05-04 | Added additional ext BPs to M90L-30K price sheet
2018-05-03 | Updated M90L MBP pricing
2018-04-30 | Updated M90 MBP pricing.
2018-04-05 | Updated J60 Warranty
2018-03-27 | Added P80-3000V2 to the P80 Price sheet.
2018-03-19 | Added V80 TAA Compliant sheet.
2018-03-16 | Updated M90L price sheet to reflect 15, 30, and 45KVA UPS accessories.
2018-03-16 | Updated prices of XPDU
2018-03-15 | Changed the description of the M90-COM card on the M90 price sheet
2018-03-12 | Corrected rail kit for P90-HT.
2018-03-01 | Added M90-COMM card to M90 price sheet
2018-02-14 | Corrected list price of P90Lg-3KTB
2018-02-06 | Corrected P/N of CC Power 90841 MBP switches
1/25/2018. | Deleted XVT Product line
2018-01-03 | Corrected P90L-BP240 dims and weight.
2017-12-28 | Added XPDS1015HV to XPDU price sheet. Adjusted price of XPDS1020HV.
2017-12-01 | Corrected dims on M90L BC55 battery cabinets
2017-11-24 | Updated P90 runtimes.
2017-11-21 | Updated J60 description to reflect 5yr warranty and charger functions
2017-11-16 | Updated J60 price, and standard 5yr warranty. Adjusted M90-40K runtimes
2017-11-08 | Added note about XC clearance .40 mult
2017-10-17 | Corrected dims on M90 480/208 transformers
2017-10-13 | Added replacement battery and battery tray weights to battery price sheet.
2017-10-11 | Added wallmount bracket to V80 price sheet.
2017-09-26 | Added M90 15KVA power module, and bundles to M90 price sheet.
2017-09-20 | Removed obsolete J40S from PDU price sheet
2017-09-15 | Changed descripion of P90-WMB to include P80, and EBMs. Also added it to P80 price sheet.
2017-09-08 | Added Seismic Anchor Kit to M90 Price Sheet.
2017-09-06 | Updated M90 MBP pricing.
2017-08-30 | Added 5yr startup and warranty to M90 Price Sheet.
2017-08-29 | Added P80-2000 to P80 Price sheet and adjusted runtimes of all P80 units
2107-08-15 | Added P90c 1U UPS to P90 Price sheet
2017-08-14 | Added T91. Deleted T90 as obsolete
2017-08-04 | Corrected XBDM-HW30 p/n from 90000089 to 90000947
2017-08-02 | Revised battery price sheet to reflect new NXRT battery tray pricing
2017-07-21 | Added 3yr service plans to M90 price sheet
2017-07-18 | Added V80 and M90 UPS systems.
2017-07-02 | Corrected Dims on P90, P90G, P90L, P80, P80G prices sheets.
2017-06-26 | Added optional line cords to J40 Series price sheets.
2017-06-17 | Added Zlock Modular Dongles to P80g and P90G price sheets.
2017-06-20 | Added SPD-0815 and SPD-1615 to XPDU pricesheet
2017-06-09 | Deleted T90-3K as obsolete.
2017-06-08 | Removed R91 transfomer due to 12 weeks lead time.
Changed listing to CE on J60i-350
2017-05-16 | Changed R91 description to include rail kit rather than shelf kit.
2017-05-10 | Added R91 to the R90 Price sheet and changed the name of the R90 tab to 3-Phase.
2017-05-04 | Added P80 and Smart PDU bundles to P80 Price list
2017-04-24 | Added P80-2200 and XPD-0815SL Bundle to P80 Price list.
2017-04-17 | Changed description of TX90-6KB5 and TX90-10KB5 to include 5-15/20R receptacles
2017-04-05 | Added SPD-0215 to the PDU Price Sheet
2017-03-28 | Revised NXRT 7.2AH battery price.
Added P80 Battery Packs and J60 Battery to Battery Price list
Added T90-WMB to T90 price list
2017-03-09 | Added P90L-6KTB4
2017-03-08 | Added J60i-350
2017-03-06 | Updated pricing on P80, P90, S70, P80G, P90L, and P90G.
Added P90-1500TB bundle
2017-02-10 | Added P90g-1500 product
Changed J60 to include standard 3ft line cord and UL/cUL listing, and deleted $25K load protection policy.
2017-02-09 | Added B5 and B6 bundles to the TX90 6&10K price sheet.
2016-12-07 | Added P90HT Product
Deleted XVRT Product line
Delteted all NXRT line items except NXRT 1000 and 2000 and associated battery packs.
Corrected P80g-5K EBM from P90G-BP72X p/nto P80G-BP72X
2016-10-26 | Changed description of P80G-5KTB to include rail kits.
2016-09-30 | Corrected P/N and price on P90G-3KTB and P90LG-3KTB
2016-09-19 | Added Replacement Battery Price Sheet
2016-08-31 | Corrected P80-2.2K description to read 2KVA/2KW
Corrected S70-2000 P/N to: 90000174
2016-08-26 | Changed description of P80G-5KTB and XPD-IT60A to reflect Maximum 120V output of 4KW
Corrected J40, J40S and J40SP prices
Added J40, J40S and J40SP to XPDU price sheet.
2016-08-17 | Added P90-2PRAIL to P80, P90, P90L and NXRT price sheets
2016-07-26 | Removed "frequency converter capability" from Parallel TX90 and T90 bundled systems.
Changed TX90 and T90 parallel system descriptions slightly for grammar and clarity improvement
2016-06-24 | Changed P/N P80G-5KB3 to P80G-5KTB
2016-06-21 | Changed length of C13-5-15P to 6ft.
2016-06-21 | Added P80G-5KB3 and XPD-IT60A to P80 price sheet.
2016-06-01 | Added SNMP-2PMINI and SNMP-EMD to P80 and P90 price sheets.
Revised runtime description on TX90-10KB4XX
2016-05-12 | Revised (3) XPRT 6-10K part numbers
2016-04-26 | Added 9000 P/Ns to all sheets.
2016-04-18 | Added P90-FRMB to P80 and P90 price sheets
Revised T90240CHG description to reflect "optional 240V input power cord".
2016-04-06 | Revised P90L-ISO6MB to include output L6-30R cord, 1ft long.
Revised T90 and TX90 6&10K to reflect increased price and addition of TX90-XR models with long runtime.
2016-03-30 | Revised depth dimension on TX90 6 & 10K.
2016-03-01 | Added P80 to Line Interactive Price Sheet
2016-02-02 | Revised description of TX90 6&10K 5yr onsite service plan to reflect that it can only be sold with a TX90 UPS 5yr service plan
2016-01-21 | Corrected T90-1500HW pricing from $1,019 to $1,099
2016-01-20 | Added BP36 and BP36E to the P90L 1-3K Price list
2016-01-06 | Lowered price on EBP battery packs on P90 and P90L 1-3K price sheets
Added "Auto Restart" to description of S70
Added "Plastic case" to descriptions of Vaue PDUs.
2015-10-16 | Added C60 and C60i to Standby price sheet.
2015-10-08 | Added P90G-3KTB and P90Lg-3KTB, UPS and Transformer PDU bundled P/Ns to P90 and P90L 1-3K price sheets
2015-10-02 | Changed description of TX90 1-3K to remove "CE" listing.
2015-08-15 | Changed description on XPRT 6&10K to reflect 208/120V or 240/120V in and out.
2015-07-15 | Added SNMP-USB card to XST and S70 price sheets
2015-06-10 | Changed NXRT-CBPx description to recommend (1) CBPx per (2) EBPx modules.
Added P90L-6KH and P90L-10KH UPSs with 4A chargers to P90L price sheets
Added XPD24C13V to PDU price sheet
Added T9VCNFG voltage configuration adder to TX90 price sheet
Added XPC racks to the "All" tab. Also added new tab for "Racks".
2015-05-05 | Changed the TX90 6&10K "XX" 120V receptacle designators to match the regular price sheet.
2015-04-23 | Removed "FCC" approval from P90, P90L 1.5-3K and associated EBMs
2015-04-02 | Changed T90 6&10 descriptions to include (no neutral or 120V available on output).
2015-04-01 | Changed Service Plan descriptions to be more specific on Electronics/Battery coverage
2015-03-26 | Updated NXRT battery packs to include EBP and CBP.
2015-02-11 | Added TX90 parallel kit to TX90 and T90 6&10KVA price list
Added surge ratings on S70 line
Added detachable line cord for S70-700
Added UL/cUL for S70 1000, 1500 and 2000 models
Added EBP option for P90-2&3K on P90 price sheet
Added EBP Service plan option on P90 price sheet
Added CBP battery packs to NXRT price list
Lowered price on EBP battery packs on NXRt price list
Changed description on NXRT EBPs to reflect deletion of charger
Changed TX90 and T90 I/O box descriptions to present recept options more clearly
Corrected XPRT-6 & 10KVA to say "Includes Monitoring Software" rather than "Includes Shutdown Software"
2015-01-30 | Corrected error in XVRT service plan offering.
2015-01-26 | Corrected runtime to T90 and TX90-10K parallel systems to read 4 minutes instead of 6 minutes.
2014-12-17 | Corrected the line cord description on P90G-3000 and P60LG-3000 from "C19 to L6-20P" to C20 to L6-20P Detachable"
2014-12-08

## Index
Product
All
J60 Series 350 - 600 VA Standby UPS
A60 Series 550 -850 VA Standby UPS
S71 Series 500 - 2000VA Line Interactive UPS
V80 Series 700 - 2000VA Line Interactive UPS
P80 Series 800 - 5000VA Line Interactive UPS
J90(i) Series 1-1.5kVA Lithium On-Line UPS
P91 Series 1-3kVA Lead Acid On-Line UPS
P91 Series 1.5-3kVA Lithium On-Line UPS
P90L(g) 1.5 - 3K
T91 Series 700-3000VA On-line UPS
P91 Series 5-10kVA On-Line UPS
TX91(L) 3.8-10K
TXVR
M90S 2S, 4S, 6S
M90S-12S
Li90 Lithium Three-Phase On-Line
E91 Series 10 - 40kVA
M90C
M90(L)U - Unity PF
M90U-80 & M90U-140 Unity PF
X90-1S & 2S
XPDU & SPDU
XBDM
Replacement Battery

## ALL
2025-11-01
J60 Series Standby UPS
Part Number | MODEL | DESCRIPTION | LIST PRICE
90000465 | J60-350 | Xtreme Power J60 Series 350VA/200W Standby UPS; 120VAC; C14 inlet with C13 to 5-15P (3ft) detachable power cord; (3) 5-15R output receptacles; Lithium battery for longer life and up to 104 F operation without battery degradation; Battery Management System (BMS) insures cell voltage balancing, parallel current sharing, and overcharge/discharge protection; surge protection; Wall or Desk Mounting; UL, cUL, RoHS and TAA compliant; 5-Year Full Warranty (USA and Canada), 3-Year Full Warranty (worldwide); 6.9"W x 8.5"D x 1.25"H, 3.4 lbs | 439
90000776 | J60-600 | Xtreme Power J60 Series 600VA/360W Standby UPS; 120VAC; C14 inlet with C13 to 5-15P (3ft) detachable power cord; (3) 5-15R output receptacles; Lithium battery for longer life and up to 104 F operation without battery degradation; redundant Battery Management System (BMS) insures cell voltage balancing, parallel current sharing, and overcharge/discharge protection; surge protection; Wall or Desk Mounting; UL, cUL, RoHS and TAA compliant; 5-Year Full Warranty (USA and Canada), 3-Year Full Warranty (worldwide); 7.3"W x 10.8"D x 1.6"H, 4.7 lbs | 749
90000472 | J60i-350 | Xtreme Power J60i Series 350VA/200W Standby UPS; 230VAC; C14 inlet; (2) IEC C13 output receptacles; Lithium battery for longer life and up to 104 F operation without battery degradation; Battery Management System (BMS) insures cell voltage balancing, parallel current sharing, and overcharge/discharge protection; surge protection; Wall or Desk Mounting; CE, RoHS and TAA compliant; 5-Year Full Warranty (USA and Canada), 3-Year Full Warranty (worldwide); 6.9"W x 8.5"D x 1.25"H, 3.4 lbs | 439
90000777 | J60i-600 | Xtreme Power J60i Series 600VA/360W Standby UPS; 230VAC; C14 inlet; (2) IEC C13 output receptacles; Lithium battery for longer life and up to 104 F operation without battery degradation; redundant Battery Management System (BMS) insures cell voltage balancing, parallel current sharing, and overcharge/discharge protection; surge protection; Wall or Desk Mounting; CE, RoHS and TAA compliant; 5-Year Full Warranty (USA and Canada), 3-Year Full Warranty (worldwide); 7.3"W x 10.8"D x 1.6"H, 4.7 lbs | 749
90001061 | J60C-600 | Xtreme Power J60C Series 600VA/360W Lithium Ion UPS; 1U; 120VAC; detachable 6' input line cord with 5-15P; (5) 5-15R output receptacles, (4 battery backup, 1 surge only); Full Load Runtime = 6 min; up to 98% efficiency; Tower, Wall, or Rack mounting; Smart LCD display; Intelligent slot; USB port; UL, cTUVus, RoHSCE, RoHS, FCC , TAA Compliant; 5-Year Full Warranty (USA and Canada), 3-Year Full Warranty (worldwide); 17.2" x 8.5" x 1.7"; 7.8 lbs | 835
90001062 | J60Ci-600 | Xtreme Power J60Ci Series 600VA/360W Lithium Ion UPS; 1U; 230VAC; IEC C14 Inlet; (5) C13 output receptacles, (4 battery backup, 1 surge only); Full Load Runtime = 6 min; up to 98% efficiency; Tower, Wall, or Rack mounting; Smart LCD display; Intelligent slot; USB port; CE, RoHS, TAA Compliant; 5-Year Full Warranty (USA and Canada), 3-Year Full Warranty (worldwide); 17.2" x 8.5" x 1.7"; 7.8 lbs | 835
900007742 | JX-200 | J60 200W Isolation Transformer, 120 VAC, 50/60Hz, C14 inlet with removeable 5-15P line cord; (3) 5-15R output receptacles; 5A output breaker; complete line isolation; Common Mode and Normal Mode noise filtering; 300 joules surge suppression; UL16950, RoHS; 5-Year Full Warranty; 6.9" W x 8.5" D x 1.25" H; 6.6 lbs. | 220
90000741 | SNMP-2PV3 | Internal SNMP/WEB Card for use with J60C and J60Ci Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-EMPV2 Environmental Monitor; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 359
90000674 | SNMP-EMPV2 | Environmental Monitoring Sensor to monitor room temperature and humidity - used with SNMP-2PV3 SNMP/WEB Card. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 230
90000778 | SNMP-J60 | External SNMP/Web Card for use with J60-600(i) Series UPS; monitor critical UPS parameters, alarms, and status; output power control to reboot loads; packaging = 7.5"W x 6"D x 2.5"H, 1 lb | 279
90000785 | EMD-J60 | Environmental Monitoring Sensor to monitor ambient temperature and humidity. Include two user defined contact closures. Must be used with SNMP-J60 External SNMP Card. Packaging = 5.7"W x 5.2"D x 1.7"H, 1 lb | 195
N/A | XPC-515P-3RA | Optional 3ft, 5-15P line cord with right angle offset for use with J60-350. Weight: .5 lbs | 22
N/A | XPC-515P-6RA | Optional 6ft, 5-15P line cord with right angle offset for use with J60-350. Weight: .5 lbs | 22
90000090 | XBDM-1015LV | Xtreme Power XBDM Series 15 Amp Maintenance Bypass Distribution Module with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of BDM + (4) 5-15R output receptacles on rear of BDM; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads;3-Year Warranty (USA and Canada); 19"W x 3.5"D x 1.75"H, 3.5 lbs For use with 700VA, 1000VA, 1500VA V80 Series | 379
90000041 | XPD1415HV | Xtreme Power XPDU Series Basic Power PDU with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of PDU + (8) 5-15R output receptacles on rear of PDU; UL60950-1/cUL/FCC Approved; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 3.5 lbs | 138
90000765 | J60-DIN | DIN Rail mount for J60 | 19
A60 - Standby UPS
Part Number | MODEL | DESCRIPTION | LIST PRICE
90000875 | A60-550 | Xtreme Power A60 Series 550VA/330W Standby UPS 120VAC; 6' Input line cord with 5-15P plug; (10) 5-15R output receptacles, (5 battery backup + 5 surge only); Tower, Desk or Wall Mounting; USB Port, Communication Cable and Shutdown Software; UL, cUL, RoHS approved, TAA Compliant; 3 Year Full Warranty (USA and Canada only); $25K Load Protection Policy; 6.2"W x 12"D x 3.7"H, 5.7 lbs | 125
90000876 | A60-850 | Xtreme Power A60 Series 850VA/500W Standby UPS 120VAC; 6' Input line cord with 5-15P plug; (10) 5-15R output receptacles, (5 battery backup + 5 surge only); Tower, Desk or Wall Mounting; touch screen display; USB Charging Port; USB Communication Port, Communication Cable and Shutdown Software; UL, cUL, RoHS approved, TAA Compliant; 3 Year Full Warranty (USA and Canada only); $25K Load Protection Policy; 6.2"W x 12"D x 3.7"H, 6.4 lbs | 165
90000281 | SNMP-USB | External SNMP/Web Card for use with A60 Series UPS; packaging = 7.5"W x 6"D x 2.5"H, 2lbs | 325
90001033 | A605SP | Xtended 5YR Factory Warranty for A60 Series UPS (USA Only) - 5 Year Coverage includes coverge of electronics and batteries, telephone technical support, advanced exchange and ground shipment both ways. | 69
S71 Line Interactive UPS
Part Number | MODEL | DESCRIPTION | LIST PRICE
90001237 | S71-700 | XPC S71 Series 700VA/420W Line-Interactive Tower UPS 120VAC; 6' detachable Input line cord with 5-15P plug; (4) 5-15R output receptacles; touch LCD display; 465 Joule surge suppression rating; Auto Restart; USB Port, Communications Cable and Shutdown Software; UL/cUL listed, RoHS, TAA Compliant; 3-Year Full Warranty (USA and Canada); $25K Load Protection Policy; 3.9"W x 11.3"D x 5.6"H, 11.2 lbs | 189
90001238 | S71-1000 | XPC S71 Series 1000VA/600W Line-Interactive Tower UPS 120VAC; 6' Input line cord with 5-15P plug; (6) 5-15R output receptacles; touch LCD display; 465 Joule surge suppression rating; Auto Restart; USB Port, Communications Cable and Shutdown Software; RJ45 Surge protection port; UL/cUL listed, RoHS, TAA Compliant; 3-Year Full Warranty (USA and Canada); $25K Load Protection Policy; 5.1"W x 12.6"D x 5.6"H, 18.0 lbs | 275
90001240 | S71-1500 | XPC S71 Series 1500VA/900W Line-Interactive Tower UPS 120VAC; 6' Input line cord with 5-15P plug; (6) 5-15R output receptacles; touch LCD display; 465 Joule surge suppression rating; Auto Restart; USB Port, Communications Cable and Shutdown Software; RJ45 Surge protection port; UL/cUL listed, RoHS, TAA Compliant; 3-Year Full Warranty (USA and Canada); $25K Load Protection Policy; 5.1"W x 12.6"D x 7.1"H, 23.0 lbs | 389
90000281 | SNMP-USB | External SNMP/Web Card for use with XST or S70 Series UPS; packaging = 7.5"W x 6"D x 2.5"H, 2 lbs | 325
90000248 | S715SP57 | Xtended 5YR Factory Warranty for S71-700 (USA and Canada) - 5 Year Coverage includes coverage of electronics and batteries, telephone technical support, advanced exchange and ground shipping both ways. | 95
90000249 | S715SP152 | Xtended 5YR Factory Warranty for S71-1000/1500 (USA and Canada) - 5 Year Coverage includes coverage of electronics and batteries, telephone technical support, advanced exchange and ground shipping both ways.. | 140
V80 Series Line Interactive UPS LA Batteries
Part Number | MODEL | DESCRIPTION | LIST PRICE
90000853 | V80-700 | Xtreme Power V80 Series 700VA/420W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable batteries; 1-6A adjustable charger; Full Load Runtime = 2.3 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 24 lbs | 499
90000890 | V80-700XR1 | Xtreme Power V80 Series 700VA/420W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable batteries; 1-6A adjustable charger; Full Load Runtime = 4.3 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 25.5 lbs | 565
90000891 | V80-700XR2 | Xtreme Power V80 Series 700VA/420W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable batteries; 1-6A adjustable charger; Full Load Runtime = 13 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 31 lbs | 625
90000892 | V80-700XR3 | Xtreme Power V80 Series 700VA/420W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable batteries; 1-6A adjustable charger; Full Load Runtime = 21 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 37 lbs | 685
90000893 | V80-700XR4 | Xtreme Power V80 Series 700VA/420W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable batteries; 1-6A adjustable charger; Full Load Runtime = 22 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 43 lbs | 745
90000854 | V80-1000 | Xtreme Power V80 Series 1000VA/600W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable batteries; 1-6A adjustable charger; Full Load Runtime = 2.7 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 27.3 lbs | 659
90000894 | V80-1000XR1 | Xtreme Power V80 Series 1000VA/600W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable batteries; 1-6A adjustable charger; Full Load Runtime = 6.0 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 31.3 lbs | 755
90000895 | V80-1000XR2 | Xtreme Power V80 Series 1000VA/600W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable batteries; 1-6A adjustable charger; Full Load Runtime = 16.0 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 43 lbs | 865
90000855 | V80-1500 | Xtreme Power V80 Series 1500VA/900W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable batteries; 1-6A adjustable charger; Full Load Runtime = 1.6 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 29.3 lbs | 749
90000896 | V80-1500XR1 | Xtreme Power V80 Series 1500VA/900W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable batteries; 1-6A adjustable charger; Full Load Runtime = 3.8 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 32.3 lbs | 809
90000897 | V80-1500XR2 | Xtreme Power V80 Series 1500VA/900W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable batteries; 1-6A adjustable charger; Full Load Runtime = 11 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 32.3 lbs | 949
90000856 | V80-2000 | Xtreme Power V80 Series 2000VA/1200W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C19 to 5-20 input line cord; (8) 5-15R output receptacles ; Hot Swappable batteries; 1-6A adjustable charger; Full Load Runtime = 1.6 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 31.3 lbs | 869
90000898 | V80-2000XR1 | Xtreme Power V80 Series 2000VA/1200W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C19 to 5-20 input line cord; (8) 5-15R output receptacles ; Hot Swappable batteries; 1-6A adjustable charger; Full Load Runtime = 1.7 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 34.3 lbs | 899
90000899 | V80-2000XR2 | Xtreme Power V80 Series 2000VA/1200W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C19 to 5-20 input line cord; (8) 5-15R output receptacles ; Hot Swappable batteries; 1-6A adjustable charger; Full Load Runtime = 4.4 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 46.3 lbs | 1039
V80 Lithium 700-1500 SERIES - 120 Volt with Lithium Batteries
Part Number | MODEL | DESCRIPTION | LIST PRICE
90000857 | V80-0.7kLi1 | Xtreme Power V80 Series 700VA/420W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable LiFeP04 batteries; 1-6A adjustable charger; Full Load Runtime = < 3 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 5 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 21.2 lbs | 999
90000967 | V80-0.7kLi2 | Xtreme Power V80 Series 700VA/420W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable LiFeP04 batteries; 1-6A adjustable charger; Full Load Runtime = 16 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 5 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 23.4 lbs | 1399
90000968 | V80-0.7kLi3 | Xtreme Power V80 Series 700VA/420W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable LiFeP04 batteries; 1-6A adjustable charger; Full Load Runtime = 18 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 5 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 25.6 lbs | 1799
90000969 | V80-0.7kLi4 | Xtreme Power V80 Series 700VA/420W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable LiFeP04 batteries; 1-6A adjustable charger; Full Load Runtime = 22 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 5 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 27.8 lbs | 2199
90000858 | V80-1kLi1 | Xtreme Power V80 Series 1000VA/600W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable LiFeP04 batteries; 1-6A adjustable charger; Full Load Runtime = 7 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 5 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 24.2 lbs | 1549
90000970 | V80-1kLi2 | Xtreme Power V80 Series 1000VA/600W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable LiFeP04 batteries; 1-6A adjustable charger; Full Load Runtime = 20 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 5 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 28.6 lbs | 2349
90000859 | V80-1.5kLi1 | Xtreme Power V80 Series 1500VA/900W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable LiFeP04 batteries; 1-6A adjustable charger; Full Load Runtime = <3 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 5 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 26 lbs | 1639
90000971 | V80-1.5kLi2 | Xtreme Power V80 Series 1500VA/900W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable LiFeP04 batteries; 1-6A adjustable charger; Full Load Runtime = 11 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 5 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 30.4 lbs | 2439
V80HT Series 700-2000 - 120 Volt with Lead Acid High Temperature Batteries
Part Number | MODEL | DESCRIPTION | LIST PRICE
90000864 | V80-700HT1 | Xtreme Power V80 Series 700VA/420W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable High Temperature Batteries; 1-6A adjustable charger; Full Load Runtime = 3.6 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 25.5 lbs | 579
90000861 | V80-700HT2 | Xtreme Power V80 Series 700VA/420W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable High Temperature Batteries; 1-6A adjustable charger; Full Load Runtime = 10 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 31 lbs | 689
90000862 | V80-700HT3 | Xtreme Power V80 Series 700VA/420W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable High Temperature Batteries; 1-6A adjustable charger; Full Load Runtime = 21 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 37 lbs | 799
90000863 | V80-700HT4 | Xtreme Power V80 Series 700VA/420W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable High Temperature Batteries; 1-6A adjustable charger; Full Load Runtime = 22 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 43 lbs | 909
90000865 | V80-1000HT1 | Xtreme Power V80 Series 1000VA/600W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable High Temperature Batteries; 1-6A adjustable charger; Full Load Runtime = 4.9 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 31.3 lbs | 799
90000864 | V80-1000HT2 | Xtreme Power V80 Series 1000VA/600W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable High Temperature Batteries; 1-6A adjustable charger; Full Load Runtime = 14.0 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 43 lbs | 1019
90000866 | V80-1500HT1 | Xtreme Power V80 Series 1500VA/900W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable High Temperature Batteries; 1-6A adjustable charger; Full Load Runtime = 3.2 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 32.3 lbs | 879
90000865 | V80-1500HT2 | Xtreme Power V80 Series 1500VA/900W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable High Temperature Batteries; 1-6A adjustable charger; Full Load Runtime = 9 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 32.3 lbs | 1099
90000867 | V80-2000HT1 | Xtreme Power V80 Series 2000VA/1200W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C19 to 5-20 input line cord; (8) 5-15R output receptacles ; Hot Swappable High Temperature Batteries; 1-6A adjustable charger; Full Load Runtime = 1.7 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 34.3 lbs | 999
90000966 | V80-2000HT2 | Xtreme Power V80 Series 2000VA/1200W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C19 to 5-20 input line cord; (8) 5-15R output receptacles ; Hot Swappable High Temperature Batteries; 1-6A adjustable charger; Full Load Runtime = 4.4 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 46.3 lbs | 1219
V80 Series Accessories
Part Number | MODEL | DESCRIPTION | LIST PRICE
90000741 | SNMP-2PV3 | Internal SNMP/WEB Card for use with V80, P80 or P91(g) Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-EMPV2 Environmental Monitor; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 359
90000674 | SNMP-EMPV2 | Environmental Monitoring Sensor to monitor room temperature and humidity - used with SNMP-2PV3 SNMP/WEB Card. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 230
90000265 | RELAY-MINI | Dry Contact RELAY CARD with DB9 & terminal block adapter; packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 120
90000406 | XPC-2PRAIL | 2-Post Rail Kit for V80, P80, P91(g) and NXRT 800VA thru 5kVA UPS or EBM; rated for 125 lbs; 4"W x 20"D x 3"H. 5 lbs. | 102
90000116 | XPC-2POSTL | 2-Post Shelf Kit for V80, P91(g)-1000, 1500, 2000, 3000; rated for 150lbs; 21.5"W x 23.3"D x 3.5"H. 9 lbs. | 160
90000392 | PV-WMB | Wall mount bracket for use with V80, P80, P91(g) and P91L series UPSs and battery packs up to 5KVA; 4"W x 24"D x 4"H. 5 lbs. | 80
90000090 | XBDM-1015LV | Xtreme Power XBDM Series 15 Amp Maintenance Bypass Distribution Module with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of BDM + (4) 5-15R output receptacles on rear of BDM; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads;3-Year Warranty (USA and Canada); 19"W x 3.5"D x 1.75"H, 3.5 lbs For use with 700VA, 1000VA, 1500VA V80 Series | 379
90000409 | V805SP71 | Xtended 5YR Factory Warranty for V80-700 and V80-1000 (USA and Canada) - 5 Year Coverage includes coverage of electronics and internal batteries, telephone technical support, advanced exchange and ground shipping both ways. | 225
90000410 | V805S52 | Xtended 5YR Factory Warranty for V80-1500 and V80-2000 (USA and Canada) - 5 Year Coverage includes coverage of electronics and internal batteries, telephone technical support, advanced exchange and ground shipping both ways. | 360
90000409 | V80HT5SP71 | Xtended 5YR Factory Warranty for V80-700 and V80-1000 (USA and Canada) - 5 Year Coverage includes coverage of electronics and internal batteries, telephone technical support, advanced exchange and ground shipping both ways. | 225
90000410 | V80HT5SP52 | Xtended 5YR Factory Warranty for V80HT-1500 and V80HT-2000 (USA and Canada) - 5 Year Coverage includes coverage of electronics and internal batteries, telephone technical support, advanced exchange and ground shipping both ways. | 360
P80 Series Line Interactive UPS
Part Number | MODEL | DESCRIPTION | LIST PRICE
90000900 | P80-800 | Xtreme Power P80 Series 800VA/720W; Line-Interactive UPS; true Sinewave output; 2U; 120VAC; 1.5A charger; Full Load Runtime = 4 min; 6' input line cord with 5-15 plug; (8) 5-15R output receptacles; Tower and rack mounting; 97% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; UL, cUL, RoHS approved; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 15.1"D x 3.5"H; 29 lbs | 789
90000901 | P80-1100 | Xtreme Power P80 Series 1100VA/990W; Line-Interactive UPS; true Sinewave output; 2U; 120VAC; 1.5A charger; Full Load Runtime = 3 min; 6' input line cord with 5-15 plug; (8) 5-15R output receptacles; Tower and rack mounting; 97% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; UL, cUL, RoHS approved; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 15.1"D x 3.5"H; 30 lbs | 849
90000902 | P80-1500 | Xtreme Power P80 Series 1500VA/1350W; Line-Interactive UPS; true Sinewave output; 2U; 120VAC; 1.5A charger; Full Load Runtime = 4 min; 6' input line cord with 5-15 plug; (8) 5-15R output receptacles; Tower and rack mounting; 97% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; UL, cUL, RoHS approved; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 18.9"D x 3.5"H; 43 lbs | 1099
90000955 | P80-2000 | Xtreme Power P80 Series 2000VA/1800W; Line-Interactive UPS; true Sinewave output; 2U; 120VAC; 1.5A charger; Full Load Runtime = 4 min; 6' input line cord with 5-20 plug; (8) 5-15/20R output receptacles; Tower and rack mounting; 97% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; UL, cUL, RoHS approved; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 18.9"D x 3.5"H; 48 lbs | 1249
90000903 | P80-2200 | Xtreme Power P80 Series 2200VA/2000W; Line-Interactive UPS; true Sinewave output; 2U; 120VAC; 1.5A charger; Full Load Runtime = 4 min; 6' input line cord with 5-20 plug; (8) 5-15/20R output receptacles; Tower and rack mounting; 97% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; UL, cUL, RoHS approved; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 23.6"D x 3.5"H; 68 lbs | 1569
90000904 | P80-3000 | Xtreme Power P80 Series 3000VA/2700W; Line-Interactive UPS; true Sinewave output; 2U; 120VAC; 1.5A charger; Full Load Runtime = 4 min; 6' input line cord with L5-30 plug; (8) 5-15/20R output receptacles; Tower and rack mounting; 97% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; UL, cUL, RoHS approved; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 23.6"D x 3.5"H; 71 lbs | 1729
90000529 | P80-3000V2 | Xtreme Power P80 Series 3000VA/2700W; Line-Interactive UPS; true Sinewave output; 2U; 120VAC; 1.5A charger; Full Load Runtime = 4 min; 6' input line cord with L5-30 plug; (6) 5-15/20R and (1) L5-30R output receptacles; Tower and rack mounting; 97% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; UL, cUL, RoHS approved; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 23.6"D x 3.5"H; 71 lbs | 1729
90000954 | P80g-3000 | Xtreme Power P80g Series 3000VA/2700W; Line-Interactive UPS; true sinewave output; 2U; 208-240VAC; 1.5A charger; Full Load Runtime = 4 min; IEC C19 to L6-20P detachable input line cord (8 ft); (1) IEC C19 + (8) IEC C13 output receptacles; Tower and rack mounting; 99% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; CE and RoHS approved; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 23.6"D x 3.5"H. 71 lbs | 1670
Bundle | P80g-3KTB | Xtreme Power P80g Series 3000VA/2700W UPS and XPD-IT15A Bundle; Line-Interactive, true sinewave UPS with 1500VA/1500W 120V Transformer PDU; 208VAC input -208/120V output; Full Load Runtime = 4 min; System has IEC-C19 to L6-20P detachable input line cord (8 ft); Output receptacles include (1) IEC C19 + (7) IEC C13 (208V) + (16) 5-15R (120V). Rack mounting; 99% efficiency in ECO mode; 1.5A charger; UPS and PDU LCD screens; RS-232 and USB port connections; 3 year full Warranty (USA and Canada); 50K load protection policy; UPS 17.2"W x 23.6"D x 3.5"H. 71 lbs. Transformer 17.5"W x 15"D x 3.5"H , 43 lbs Package Includes: P80g-3000 UPS Power Module (2U) XPD-IT15A Transformer Module (2U) UPS to Transformer Cable C13 to C14 Software P90-Rail 4-Post Rail Kit | 2920
90000430 | P80g-5000 | Xtreme Power P80g Series 5000VA/4500W; Line-Interactive UPS; true sinewave output; 2U; 208-240VAC; 1.5A charger; Full Load Runtime = 2.5 min; L6-30P input line cord (6 ft); (1) L6-30R + (4) IEC C19 output receptacles; Tower and rack mounting; 99% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; CE and RoHS approved; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 23.6"D x 3.5"H. 85 lbs | 2750
Bundle | P80g-5KB1 | Xtreme Power P80g Series 5000VA/4500W; Line-Interactive UPS; true sinewave output; 2U; 208-240VAC; 1.5A charger; Full Load Runtime = 2.5 min; L6-30P input line cord (6 ft); (2) L6-30R + (2) L6-20R + (1) IEC C19 output receptacles; Tower and rack mounting; 99% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; CE and RoHS approved; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 23.6"D x 3.5"H. 90 lbs | 2987
Bundle | P80g-5KB2 | Xtreme Power P80g Series 5000VA/4500W; Line-Interactive UPS and XPD24C13V PDU bundle; true sinewave output; 2U; 208-240VAC; 1.5A charger; Full Load Runtime = 2.5 min; L6-30P input line cord (6 ft); (4) IEC C19 + (24) IEC C13 output receptacles; Tower and rack mounting; 99% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; CE and RoHS approved; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 23.6"D x 3.5"H. 97 lbs | 3090
Bundle | P80g-5KTB | Xtreme Power P80g Series 5000VA/4500W; Line-Interactive UPS and XPD-IT60A Transformer PDU bundle; true sinewave output; 2U; 208V or 240V in, 208/104V or 240/120V out, Max. 120V load is 4KW; 1.5A charger; Full Load Runtime = 2.5 min; L6-30P input line cord (6 ft); (2) L6-30R, (2) L6-20R and (12) 5-15/20R output receptacles; Tower and rack mounting; 99% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; CE and RoHS approved; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 23.6"D x 7"H (4U). 147 lbs. Bundle includes: P80G-5000 UPS, IT60A transformer PDU, (3) receptacle dongles, (2) 4-post rail kits. | 5427
90000916 | P90-BP48 | Extended Runtime Battery Pack for use with P80-1500, P80-2000, P90-2000 or P90L-2000 UPSs; (includes 8 each 12V9AH batteries); __ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower or Rack Mounting; TUV/UL, RoHS, cUL Approved; 3-Year Full Warranty (USA only); 17.2"W x 18.9"D x 3.5"H; 74.6 lbs | 990
90000917 | P90-BP72 | Extended Runtime Battery Pack for use with P80-2200, P80-3000, P80g-3000, or P90/P90L-3000 and P90g/P90Lg-3000 UPSs; (includes 12 each 12V9AH batteries) ;__ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower or Rack Mounting; TUV/UL, RoHS, cUL Approved; 3-Year Full Warranty (USA only); 17.2"W x 23.6"D x 3.5"H; 104.4 lbs | 1290
90000432 | P80-BP72X | Extended Runtime Battery Pack for use with P80g-5000 UPS; (includes (12) 12V 580W at 5 min rate batteries) ;__ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower or Rack Mounting; CE, RoHS Approved; 3-Year Full Warranty (USA only); 17.2"W x 23.6"D x 3.5"H; 110.4 lbs | 1720
90000909 | P90-RAIL | 4-Post Rail Kit for use with P80-800VA thru 5KVA or P90-1KVA thru 3KVA UPS or EBM; extends from 18.75" to 30.9"; Packaging 3.8"W x 19.8"D x 2.8"H. 5 lbs. | 135
90000933 | P90L-RAIL | Adjustable Mounting 4-Post Rail Kit for P91 or P90L-5K, 6K, &10K UPS, BP & Transformer Module; extends from 21" to 35.5"; packaging = 3..8"W x 22"D x 2.8"H, 5 lbs | 149
90000406 | XPC-2PRAIL | 2-Post Rail Kit for P80, P90, P90L and NXRT 800VA thru 5kVA UPS or EBM; rated for 125 lbs; 4"W x 20"D x 3"H. 5 lbs. | 102
90000116 | XPC-2POSTL | 2-Post Shelf Kit for P80-800VA thru 5kVA or P90-1KVA thru 3KVA UPS or EBM; rated for 150 lbs; 21.5"W x 23.3"D x 3.5"H. 9 lbs. | 160
90001273 | XPC-2PRLV2 | 2-Post Shelf Kit with front ears for P80(g); rated for 160lbs; 21.5"W x 23.3"D x 3.5"H. 9 lbs. | 225
90000392 | PV-WMB | Wall mount bracket for use with P80, P90 and P90L series UPSs and battery packs up to 5KVA; 4"W x 24"D x 4"H. 5 lbs. | 80
90000377 | P90-FRMB | Front Rackmount Bracket for P80 800VA through 2KVA size or P90 1KVA thru 2KVA size. Required when front mounting the UPS to a 2 post or 4 post rack with no rail kit. | 36
90000741 | SNMP-2PV3 | Internal SNMP/WEB Card for use with P80 or P90 Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-EMPV2 Environmental Monitor; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 359
90000674 | SNMP-EMPV2 | Environmental Monitoring Sensor to monitor room temperature and humidity - used with SNMP-2PV3 SNMP/WEB Card. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 230
90000267 | MODBUS-IN | MODBUS CARD for use with the P80 or P90 Series UPS. Packaging = 7.25"W x 6"D x 2.5"H, 1 lbs | 319
90000265 | RELAY-MINI | Dry Contact RELAY CARD with DB9 & terminal block adapter. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 120
90000090 | XBDM-1015LV | Xtreme Power XBDM Series 15 Amp Maintenance Bypass Distribution Module with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of BDM + (4) 5-15R output receptacles on rear of BDM; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads;3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 379
90000091 | XBDM-1020LV | Xtreme Power XBDM Series 20 Amp Maintenance Bypass Distribution Module with 12' Input line cord with 5-20P plug; (6) 5-20R output receptacles on front of BDM + (4) 5-20R output receptacles on rear of BDM; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads; 3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 419
90000093 | XBDM-1030LV | Xtreme Power XBDM Series 30 Amp Maintenance Bypass Distribution Module with 6' Input line cord with L5-30P plug; (5) 5-20R output receptacles on front of BDM (Load Group 1) + (5) 5-20R output receptacles on rear of BDM (Load Group 2); (2) bypass switches allowing for bypassing and maintenance of the UPS without affecting the connected loads; 3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 659
90000041 | XPD1415HV | Xtreme Power XPDU Series Basic Power PDU with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of PDU + (8) 5-15R output receptacles on rear of PDU; UL60950-1/cUL/FCC Approved; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 3.5 lbs | 138
90000045 | XPD1420HV | Xtreme Power XPDU Series Basic Power PDU with 12' Input line cord with L5-20P plug (L5-20 to 5-20 adapter included); (6) 5-20R output receptacles on front of PDU + (8) 5-20R output receptacles on rear of PDU; UL60950-1/cUL/FCC Approved; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 4.8 lbs | 190
TBD | XPC-ZLC20-620R | P80g/90g Output Cord, 1ft, IEC Locking C20 to 6-15/20R. 3 lbs. | 79
TBD | XPC-ZLC20-L620R | P80g/90g Output Cord,1ft, IEC Locking C20 to L6-20R. 3 lbs. | 79
TBD | XPC-ZLC20-L630R | P80g/90g Output Cord, 1ft, IEC Locking C20 to L6-30R. 3 lbs. | 79
TBD | XPC-C14-615R | P80g/90g Output Cord, 1ft, IEC C14 to 6-15R. 3 lbs. | 45
90000094 | XBDM1020HV2 | Xtreme Power XBDM Series Maintenance Bypass Distribution Module for use with P80G-3000 or P90G-3000 UPS; C20 input receptacle; rated at 16A; (2) IEC C19 and (4) IEC C13 output receptacles on front + (4) IEC C13 output receptacles on back; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads; Includes (2) IEC C20-C19 cord kit; 3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 419
90000374 | XPD24C13V | Xtreme Power XPDU Series Basic Power PDU, 30A, 200-240V; L6-30P 6ft line cord, (24) C13 output receptacles. Vertical Mount. 1.75"W x 1.75"D x 66"L. 12 lbs | 340
90000251 | XPD31 | Xtreme Power XPDU Series Basic Power PDU, 30A, 200-240V; L6-30P 6ft line cord, (2) L6-30R, (2) L6-20R and (4) 6-15/20R output receptacles. Rackmount. 19"W x 4.7"D x 3.5"H. 9 lbs | 580
90000252 | XPD32 | Xtreme Power XPDU Series Basic Power PDU, 30A, 200-240V; L6-30P 6ft line cord, (2) L6-30R, (4) L6-20R output receptacles. Rackmount. 19"W x 2.4"D x 3.5"H. 7.5 lbs | 580
90000253 | XPD33 | Xtreme Power XPDU Series Basic Power PDU, 30A, 200-240V; L6-30P 6ft line cord, (4) IEC C19 and (8) IEC C13 output receptacles. Rackmount. 19"W x 2.4"D x 3.5"H. 8 lbs | 450
90000053 | XPDU-IEC | Xtreme Power XPDU Series Basic Power 230V PDU with C20 inlet (power cord ordered separately), (10) IEC C13 + (2) IEC C19 output receptacles; 1U Rackmount configuration; CE Listed; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 2.6 lbs | 190
90000407 | XPD-IT60A | Xtreme Power XPDU Series 6KVA PDU with Isolation Transformer for use with P80G-5000 or P91 5-10K UPS. 6000W, 208 or 240 in, 208/104V or 240/120V out. 3ft L6-30P Input Cord. (1) L6-30R and (12) 5-15-20R output receptacles; rear panel 208/240 voltage selection switch; includes front panel rackmount brackets; ROHS Approved; 3-Year Warranty; 17.3"W x 18"D x 3.5"H (2U), 137 lbs. | 1750
90000269 | XAT-400 | 400VA Step Down Transformer, 208V to 120V for P80G/P90G and P90LG-3000. Input is 208V IEC C14 on 2ft cord; output is 120V 5-15R on 2ft cord. 7"W x 6.8"D x 5.9"H. 8 lbs. | 600
90000739 | XPD-IT15A | Xtreme Power XPDU Series PDU with Isolation Transformer. 1500W, 208V in, 120V out. IEC-C14 inlet with 3' 5-15 line cord ; (16) 5-15R output receptacles protected by 15A breaker; 3-Year Warranty; 17.5"W x 15"D x 3.5"H (2U), 43 lbs. | 980
90000522 | P905SP15 | Xtended 5YR Factory Warranty for P80-800/1100/1500 or P90-1000/1500VA UPS (USA only) - 5 Year Coverage includes coverage of electronics and internal batteries, telephone technical support, advanced exchange and ground shipping both ways. | 375
90000523 | P905SP23 | Xtended 5YR Factory Warranty for P80-2000/2200/3000 and P80g-3000 or P90-2000/3000VA and P90g-3000 UPS (USA only) - 5 Year Coverage includes coverage of electronics and internal batteries, telephone technical support, advanced exchange and ground shipping both ways. | 610
90000431 | P805SP5 | Xtended 5YR Factory Warranty for P80g-5000 UPS (USA only) - 5 Year Coverage includes coverage of electronics and internal batteries, telephone technical support, advanced exchange and ground shipping both ways. | 800
90000524 | P90L5SPBP | Xtended 5YR Factory Warranty for P90-BP48/BP72 (USA only) - 5 Year Coverage includes coverage of battery pack, telephone technical support, advanced exchange and ground shipping both ways. | 320
J90(i) 1-1.5k SERIES - 120(230)volt with Lithium-ion Batteries
Part Number | MODEL | DESCRIPTION | LIST PRICE
90001298 | J90-1KLi | Xtreme Power J90 Series 1000VA/900W; Online UPS with Lithium-ion batteries; 1U; 120VAC; C14 inlet with 5' input line cord with 5-15P; (4) 5-15R individually switchable output receptacles (with optional web/SNMP card); 4 hour typical recharge; Full Load Runtime = 6.5 min; Tower , rack, or wall mounting; Smart LCD display; Intelligent slot; RS-232 and USB port; Remote On/Off connection; UL, cUL, RoHS approved; FCC Class A, UN38.3; 6-year full warranty (electronics and batteries) applies for installations where the ambient temperature remains at or below 30°C (86°F) in the USA and Canada. For environments exceeding 30°C, a 3-year warranty applies; 50K load protection policy; 17.2" x 18.8" x 1.7"; 27.3 lbs. | 2450
90001301 | J90-1.5KLi | Xtreme Power J90 Series 1500VA/1350W; Online UPS with Lithium-ion batteries; 1U; 120VAC; 6' input line cord with 5-15P; (4) 5-15R individually switchable output receptacles (with optional web/SNMP card); 4 hour typical recharge; Full Load Runtime = 7 min; Tower , rack, or wall mounting; Smart LCD display; Intelligent slot; RS-232 and USB port; Remote On/Off connection; UL, cUL, RoHS approved; FCC Class A, UN38.3; 6-year full warranty (electronics and batteries) applies for installations where the ambient temperature remains at or below 30°C (86°F) in the USA and Canada. For environments exceeding 30°C, a 3-year warranty applies; 50K load protection policy; 17.2" x 20.0" x 1.7"; 27.8 lbs. | 2730
90001299 | J90i-1KLi | Xtreme Power J90i Series 1000VA/900W; Online UPS with Lithium-ion batteries; 1U; 230VAC; C14 inlet ; (4) IEC C13 individually switchable output receptacles (with optional web/SNMP card); 4 hour typical recharge; Full Load Runtime = 6.5 min; Tower , rack, or wall mounting; Smart LCD display; Intelligent slot; RS-232 and USB port; Remote On/Off connection; CE, RoHS approved; UN38.3; 6-year full warranty (electronics and batteries) applies for installations where the ambient temperature remains at or below 30°C (86°F) in the USA and Canada. For environments exceeding 30°C, a 3-year warranty applies; 50K load protection policy; 17.2" x 18.8" x 1.7"; 26.4 lbs. | 2400
90001302 | J90i-1.5KLi | Xtreme Power J90i Series 1500VA/1350W; Online UPS with Lithium-ion batteries; 1U; 230VAC; C14 inlet ; (4) IEC C13 individually switchable output receptacles (with optional web/SNMP card); 4 hour typical recharge; Full Load Runtime = 7 min; Tower , rack, or wall mounting; Smart LCD display; Intelligent slot; RS-232 and USB port; Remote On/Off connection; CE, RoHS approved; UN38.3; 6-year full warranty (electronics and batteries) applies for installations where the ambient temperature remains at or below 30°C (86°F) in the USA and Canada. For environments exceeding 30°C, a 3-year warranty applies; 50K load protection policy; 17.2" x 20.0" x 1.7"; 27.7 lbs. | 2680
90000741 | SNMP-2PV3 | Internal SNMP/WEB Card for use with J90 or J90i Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-EMPV2 Environmental Monitor; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 359
90000674 | SNMP-EMPV2 | Environmental Monitoring Sensor to monitor room temperature and humidity - used with SNMP-2PV3 SNMP/WEB Card. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 230
90000265 | RELAY-MINI | RELAY CARD with DB9 & terminal block adapter; packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 120
90000090 | XBDM-1015LV | Xtreme Power XBDM Series 15 Amp Maintenance Bypass Distribution Module with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of BDM + (4) 5-15R output receptacles on rear of BDM; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads;3-Year Warranty (USA and Canada); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 379
90000041 | XPD1415HV | Xtreme Power XPDU Series Basic Power PDU with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of PDU + (8) 5-15R output receptacles on rear of PDU; UL60950-1/cUL/FCC Approved; 3-Year Warranty (USA and Canada); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 138
90000909 | P90-RAIL | 4-Post Rail Kit for use with P91(g)-1000, 1500, 2000, 3000; extends from 18.75" to 30.9"; packaging 3.8"W x 19.8"D x 2.8"H. 5 lbs. | 135
90001036 | P91ADVEX | Advanced Exchange Warranty Upgrade for advanced warranty exchange and shipping for J90(i) and P91(g) UPS (USA and Canada) | 250
P91 1-3K SERIES - 120 Volt with Lead Acid Batteries
Part Number | MODEL | DESCRIPTION | LIST PRICE
90000621 | P91c-1000 | Xtreme Power P91 Series 1000VA/800W; Online UPS; 1U; 120VAC; C14 inlet with 5' C13 to 5-15P input line cord; (3) 5-15R output receptacles; Hot Swappable batteries; 1A charger; Full Load Runtime = 8 min; Front mount rack brackets included; 98% efficiency in ECO mode; Smart LED display; Intelligentt slot; USB port and REPO connections; UL, cUL, RoHS approved; FCC Class A; TAA Compliant; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2" x 17.8" x 1.7"; 28 lbs | 1130
90000756 | P91-1000 | Xtreme Power P91 Series 1000VA/1000W; Online UPS; 2U; 120VAC; 6' input line cord with 5-15 plug; (8) 5-15R output receptacles, (4) of the output receptacles programmable as group ; Hot Swappable batteries; 1-8A adjustable charger; Full Load Runtime = 3 min; Tower and rack mounting; 98% efficiency in ECO mode; Smart LCD screen; Intelligent slot; RS-232, USB port, and REPO connections; UL, cUL, RoHS approved; FCC Class B; TAA Compliant; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2" x 15.1" x 3.5"; 25.5 lbs | 1165
90000622 | P91-1500 | Xtreme Power P91 Series 1500VA/1450W; Online UPS; 2U; 120VAC; 6' input line cord with 5-15 plug; (8) 5-15R output receptacles, (4) of the output receptacles programmable as group; Hot Swappable batteries; 1-8A adjustable charger; Full Load Runtime = 3 min; Tower and rack mounting; 98% efficiency in ECO mode; Smart LCD screen; Intelligent slot; RS-232, USB port, and REPO connections; UL, cUL, RoHS approved; FCC Class B; TAA Compliant; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2" x 15.1" x 3.5"; 34.2 lbs | 1520
90000623 | P91-2000 | Xtreme Power P91 Series 2000VA/1930W; Online UPS; 2U; 120VAC; 6' input line cord with 5-20 plug; (8) 5-15/20R output receptacles, (4) of the output receptacles programmable as group; Hot Swappable batteries; 1-8A adjustable charger; Full Load Runtime = 3 min; Tower and rack mounting; 98% efficiency in ECO mode; Smart LCD screen; Intelligent slot; RS-232, USB port, and REPO connections; UL, cUL, RoHS approved; FCC Class A; TAA Compliant; 3 year full Warranty (USA and Cnada); 50K load protection policy; 17.2" x 19.0" x 3.5"; 43 lbs | 1985
90000624 | P91-3000 | Xtreme Power P91 Series 3000VA/2880W; Online UPS; 2U; 120VAC; 6' input line cord with L5-30 plug; (1) L5-30R + (6) 5-15/20R output receptacles, (3) of the 5-15/20R output receptacles programmable as group; Hot Swappable batteries; 1-8A adjustable charger; Full Load Runtime = 3 min; Tower and rack mounting; 98% efficiency in ECO mode; Smart LCD screen; Intelligent slot; RS-232, USB port, and REPO connections; UL, cUL, RoHS approved; FCC Class A; TAA Compliant; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2" x 23.8" x 3.5"; 60.6 lbs. | 2650
P91g 1-3K SERIES - 208/230 Volt with Lead Acid Batteries
Part Number | MODEL | DESCRIPTION | LIST PRICE
90000746 | P91gc-1000 | Xtreme Power P91 Series 1000VA/800W; Online UPS; 1U; 230 VAC, 200/208/220/230/240VAC selectable; C14 inlet with 8' C13 to L6-20P input line cord; (3) C13 output receptacle; Hot Swappable batteries; 1A charger; Full Load Runtime = 8 min; Front mount rack brackets included; 98% efficiency in ECO mode; Smart LED display; Intelligent slot; USB port connection; CE, RoHS; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2" x 17.8" x 1.7"; 28 lbs. | 1050
90000747 | P91g-1500 | Xtreme Power P91g Series 1500VA/1500W; Online UPS; 2U; 230 VAC, 200/208/220/230/240VAC selectable; IEC-C14 Inlet with 8' IEC C13 to L6-20P detachable input line cord; (8) IEC C13 output receptacles, (4) of the output receptacles programmable as group; Hot Swappable Batteries; 1-12A adjustible charger; Full Load Runtime = 3 min; Tower and rack mounting; 98% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; CE and RoHS approved; TAA Compliant; 3 year full Warranty (USA only); 50K load protection policy; 17.2" x 15.1" x 3.5". 34.2 lbs. Capacity derates 90% for 200 or 208 VAC output. | 1399
90000748 | P91g-2000 | Xtreme Power P91 Series 2000VA/2000W; Online UPS; 2U; 230VAC, 200/208/220/230/240VAC selectable ; IEC-C20 Inlet with 8' IEC C19 to L6-20P detachable input line cord; (8) IEC C13 output receptacles, (4) of the output receptacles programmable as group; Hot Swappable batteries; 1-12A adjustable charger; Full Load Runtime = 3 min; Tower and rack mounting; 98% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; CE, RoHS approved; TAA Compliant; 3 year full Warranty (USA and Cnada); 50K load protection policy; 17.2" x 19.0" x 3.5"; 43 lbs. Capacity derates 90% for 200 or 208 VAC output. | 1829
90000749 | P91g-3000 | Xtreme Power P91g Series 3000VA/3000W; Online UPS; 2U; 230VAC, 200/208/220/230/240VAC selectable ; IEC-C20 Inlet with 8' IEC C19 to L6-20P detachable input line cord; (1) C19 + (8) IEC C13 output receptacles, (4) of the output receptacles programmable as group; Hot Swappable batteries; 1-12A adjustable charger; Full Load Runtime = 3 min; Tower and rack mounting; up to 98% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; CE, RoHS approved; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2" x 23.8" x 3.5". 60.6 lbs. Capacity derates 90% for 200 or 208 VAC output. | 2449
P91 1-3K SERIES External Batteries and Accessories
Part Number | MODEL | DESCRIPTION | LIST PRICE
90000787 | P91-BP36 | Extended Runtime Battery Pack for use with P91(g)-1500 (includes 2 strings of 12V9AH batteries); __ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower or Rack Mounting; UL, cUL, RoHS Approved; 3-Year Full Warranty (USA and Canada); 17.2"W x 18.9"D x 3.5"H; 58.1 lbs | 920
90000788 | P91-BP36E | Extended Runtime Battery Pack for use with P91(g)-1500 (includes 4 strings of 12V9AH batteries); __ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower or Rack Mounting; UL, cUL, RoHS Approved; 3-Year Full Warranty (USA and Canada); 17.2"W x 23.6"D x 3.5"H; 104.4 lbs | 1320
90000789 | P91-BP48 | Extended Runtime Battery Pack for use with P91(g)-2000 UPS; (includes 2 strings of 12V9AH batteries); __ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower or Rack Mounting; UL, cUL, RoHS Approved; 3-Year Full Warranty (USA and Canada); 17.2"W x 18.9"D x 3.5"H; 74.6 lbs | 1080
90000790 | P91-BP72 | Extended Runtime Battery Pack for use with P91-3000 and P91g-3000 UPSs; (includes 2 strings of 12V9AH batteries) ;__ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower or Rack Mounting; UL, cUL, RoHS Approved; 3-Year Full Warranty (USA and Canada); 17.2"W x 23.6"D x 3.5"H; 104.4 lbs | 1290
TBD | XPC-C14-615R | P91g Output Cord, 1ft, IEC C14 to 6-15R. 3 lbs. | 45
TBD | XPC-C14-620R | P91g Output Cord, 1ft, IEC C14 to 6-20R. 3 lbs. | 49
TBD | XPC-C14-L620R | P91g Output Cord, 1ft, IEC C14 to L6-20R. 3 lbs. | 69
TBD | XPC-C14-L630R | P91g Output Cord, 1ft, IEC C14 to L6-30R. 3 lbs. | 69
| XPC-ZLC20-620R | Optional 12" output cord, Locking C20 to 6-15/20 receptacle; 3 lbs. | 79
| XPC-ZLC20-L620R | Optional 12" output cord, Locking C20 to L6-20 receptacle; 3 lbs. | 79
| XPC-ZLC20-L630R | Optional 12" output cord, Locking C20 to L6-30 receptacle; 3 lbs. | 79
90000909 | P90-RAIL | 4-Post Rail Kit for use with P91(g)-1000, 1500, 2000, 3000; extends from 18.75" to 30.9"; packaging 3.8"W x 19.8"D x 2.8"H. 5 lbs. | 135
90000406 | XPC-2PRAIL | 2-Post Rail Kit for P80, P91(g) and NXRT 800VA thru 5kVA UPS or EBM; rated for 125 lbs; 4"W x 20"D x 3"H. 5 lbs. | 102
90000116 | XPC-2POSTL | 2-Post Shelf Kit for P91(g)-1000, 1500, 2000, 3000; rated for 150lbs; 21.5"W x 23.3"D x 3.5"H. 9 lbs. | 160
90001273 | XPC-2PRLV2 | 2-Post Shelf Kit with front ears for P91(g)-1000, 1500, 2000, 3000; rated for 160lbs; 21.5"W x 23.3"D x 3.5"H. 9 lbs. | 225
90000392 | PV-WMB | Wall mount bracket for use with P80, P91(g) and P91L series UPSs and battery packs up to 5KVA; 4"W x 24"D x 4"H. 5 lbs. | 80
90000377 | P90-FRMB | Front Rackmount Bracket for P80 800VA through 2KVA size or P91 1KVA thru 2KVA size. Required when front mounting the UPS to a 2 post or 4 post rack with no rail kit. | 36
90000741 | SNMP-2PV3 | Internal SNMP/WEB Card for use with P80 or P91(g) Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-EMPV2 Environmental Monitor; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 359
90000674 | SNMP-EMPV2 | Environmental Monitoring Sensor to monitor room temperature and humidity - used with SNMP-2PV3 SNMP/WEB Card. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 230
90000267 | MODBUS-IN | MODBUS CARD for use with the P91(g) Series UPS; packaging = 7.25" x 6" x 2.5", 1 lbs | 319
90000265 | RELAY-MINI | Dry Contact RELAY CARD with DB9 & terminal block adapter; packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 120
90000090 | XBDM-1015LV | Xtreme Power XBDM Series 15 Amp Maintenance Bypass Distribution Module with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of BDM + (4) 5-15R output receptacles on rear of BDM; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads;3-Year Warranty (USA and Canada); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 379
90000091 | XBDM-1020LV | Xtreme Power XBDM Series 20 Amp Maintenance Bypass Distribution Module with 12' Input line cord with 5-20P plug; (6) 5-20R output receptacles on front of BDM + (4) 5-20R output receptacles on rear of BDM; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads; 3-Year Warranty (USA and Canada); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 419
90000093 | XBDM-1030LV | Xtreme Power XBDM Series 30 Amp Maintenance Bypass Distribution Module with 6' Input line cord with L5-30P plug; (5) 5-20R output receptacles on front of BDM (Load Group 1) + (5) 5-20R output receptacles on rear of BDM (Load Group 2); (2) bypass switches allowing for bypassing and maintenance of the UPS without affecting the connected loads; 3-Year Warranty (USA and Canada); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 659
90000041 | XPD1415HV | Xtreme Power XPDU Series Basic Power PDU with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of PDU + (8) 5-15R output receptacles on rear of PDU; UL60950-1/cUL/FCC Approved; 3-Year Warranty (USA and Canada); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 138
90000045 | XPD1420HV | Xtreme Power XPDU Series Basic Power PDU with 12' Input line cord with L5-20P plug (L5-20 to 5-20 adapter included); (6) 5-20R output receptacles on front of PDU + (8) 5-20R output receptacles on rear of PDU; UL60950-1/cUL/FCC Approved; 3-Year Warranty (USA and Canada); 19"W x 3.5"D x 1.75"H, 4.8 lbs | 190
90000094 | XBDM1020HV2 | Xtreme Power XBDM Series Maintenance Bypass Distribution Module with C20 input receptacle; rated at 16A; (2) IEC C19 and (4) IEC C13 output receptacles on front + (4) IEC C13 output receptacles on back; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads; Includes (2) IEC C20C19 cord kit; 3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 419
90000053 | XPDU-IEC | Xtreme Power XPDU Series Basic Power 230V PDU with C20 inlet (power cord ordered separately), (10) IEC C13 + (2) IEC C19 output receptacles; 1U Rackmount configuration; CE Listed; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 2.6 lbs | 190
90000269 | XAT-400 | 400VA Step Down Transformer, 208V to 120V for P90G and P90LG-3000. Input is 208V IEC C14 on 2ft cord; output is 120V 5-15R on 2ft cord. 7"W x 6.8"D x 5.9"H. 8 lbs. | 600
90000739 | XPD-IT15A | Xtreme Power XPDU Series PDU with Isolation Transformer. 1500W, 208V in, 120V out. IEC-C14 inlet with 3' 5-15 line cord ; (16) 5-15R output receptacles protected by 15A breaker; 3-Year Warranty; 17.5"W x 15"D x 3.5"H (2U), 43 lbs. | 980
90000877 | P915SP15 | Xtended 5YR Factory Warranty forP91c-1000, P91-1000, P91-1500 UPS (USA and Canada) - 5 Year Coverage includes coverage of electronics and internal batteries, telephone technical support, advanced exchange and ground shipping both ways. | 375
90000878 | P915SP23 | Xtended 5YR Factory Warranty for P91-2000/3000VA and P91g-3000 UPS (USA and Canada) - 5 Year Coverage includes coverage of electronics and internal batteries, telephone technical support, advanced exchange and ground shipping both ways. | 610
90000879 | P91L5SPBP | Xtended 5YR Factory Warranty for P91-BP36/BP36E/BP42/BP72 (USA and Canada) - 5 Year Coverage includes coverage of battery pack, telephone technical support, advanced exchange and ground shipping both ways.. | 320
P91 1-3K SERIES - 120 Volt with Lithium-ion Batteries
Part Number | MODEL | DESCRIPTION | LIST PRICE
90000750 | P91-1.5KLi | Xtreme Power P91 Series 1500VA/1350W; Online UPS with Lithium-ion batteries; 2U; 120VAC; 6' input line cord with 5-15P; (8) 5-15R output receptacles, (4) of the output receptacles programmable as group; 1-8A adjustable charger; Full Load Runtime = 8 min; Tower and rack mounting; up to 98% efficiency in ECO mode; Smart LCD screen; Intelligent slot; RS-232 and USB port; REPO connection; UL, cUL, RoHS, FCC Class A, UN38.3 for battery transportation; 6 year full Warranty (USA and Canada), 1 year full Warranty (worldwide); 50K load protection policy; 17.2" x 15.1" x 3.5"; 25.6 lbs | 2520
90000751 | P91-2KLi | Xtreme Power P91 Series 2000VA/1800W; Online UPS with Lithium-ion batteries; 2U; 120VAC; 6' input line cord with 5-20 plug; (8) 5-15/20R output receptacles, (4) of the output receptacles programmable as group; 1-8A adjustable charger; Full Load Runtime = 14 min; Tower and rack mounting; 98% efficiency in ECO mode; Smart LCD screen; Intelligent slot, RS-232 and USB port connections; REPO connection; UL, cUL, RoHS, FCC Class A, UN38.3 for battery transportation; 6 year full Warranty (USA and Canada), 1 year full Warranty (worldwide); 50K load protection policy; 17.2" x 19.0" x 3.5"; 33.5 lbs | 3730
90000752 | P91-3kLi | Xtreme Power P91 Series 3000VA/2700W; Online UPS with Lithium-ion batteries; 2U; 120VAC; 6' input line cord with L5-30 plug; (1) L5-30R + (6) 5-15/20R output receptacles, (3) of the 5-15/20R output receptacles programmable as group; 1-8A adjustable charger; Full Load Runtime = 11 min; Tower and rack mounting; 98% efficiency in ECO mode; Smart LCD screen; Intelligent slot, RS-232 and USB port connections, REPO connection; UL, cUL, RoHS, FCC Class A, UN38.3 for battery transportation; 6 year full Warranty (USA and Canada); 50K load protection policy; 17.2" x 23.8" x 3.5"; 45.2 lbs. | 4570
P91g 1-3K SERIES - 208/230 Volt with Lithium-ion Batteries
Part Number | MODEL | DESCRIPTION | LIST PRICE
90000753 | P91g-1.5KLi | Xtreme Power P91 Series 1500VA/1350W; Online UPS with Lithium-ion batteries; 2U; 208/230VAC; C14 Inlet with 8' C13 to L6-20P line cord ; (8) IEC C13 output receptacles, (4) of the output receptacles programmable as group; 1-8A adjustable charger; Full Load Runtime = 8 min; Tower and rack mounting; up to 98% efficiency in ECO mode; Smart LCD screen; Intelligent slot; RS-232 and USB port; REPO connection; CE, RoHS, FCC Class A, UN38.3 for battery transportation; 6 year full Warranty (USA and Canada); 50K load protection policy; 17.2" x 15.1" x 3.5"; 25.6 lbs | 2470
90000754 | P91g-2KLi | Xtreme Power P91 Series 2000VA/1800W; Online UPS with Lithium-ion batteries; 2U; 208/230VAC; C20 Inlet with 8' C19 to L6-20P line cord ; (8) IEC C13 output receptacles (4) of the output receptacles programmable as group; 1-8A adjustable charger; Full Load Runtime = 14 min; Tower and rack mounting; 98% efficiency in ECO mode; Smart LCD screen; Intelligent slot, RS-232 and USB port connections; REPO connection; CE, RoHS, FCC Class A, UN38.3 for battery transportation; 6 year full Warranty (USA and Canada), 1 year full Warranty (worldwide); 50K load protection policy; 17.2" x 19.0" x 3.5"; 33.5 lbs | 3680
90000755 | P91g-3kLi | Xtreme Power P91 Series 3000VA/2700W; Online UPS with Lithium-ion batteries; 2U; 208/230VAC; C20 Inlet with 8' C19 to L6-20P line cord ; (1) IEC C19,(8) IEC C13 output receptacles, (4) of the C13 output receptacles programmable as group; 1-8A adjustable charger; Full Load Runtime = 11 min; Tower and rack mounting; 98% efficiency in ECO mode; Smart LCD screen; Intelligent slot, RS-232 and USB port connections, REPO connection; CE, RoHS, FCC Class A, UN38.3 for battery transportation; 6 year full Warranty (USA and Canada), 1 year full Warranty (worldwide); 50K load protection policy; 17.2" x 23.8" x 3.5"; 45.2 lbs. | 4520
TBD | XPC-C14-615R | P91g Output Cord, 1ft, IEC C14 to 6-15R. 3 lbs. | 45
TBD | XPC-ZLC20-620R | Optional 12" output cord, Locking C20 to 6-15/20 receptacle for use with P91g-3kLi; 3 lbs. | 79
TBD | XPC-ZLC20-L620R | Optional 12" output cord, Locking C20 to L6-20 receptacle for use with P91g-3kLi; 3 lbs. | 79
TBD | XPC-ZLC20-L630R | Optional 12" output cord, Locking C20 to L6-30 receptacle for use with P91g-3kLi; 3 lbs. | 79
90000909 | P90-RAIL | 4-Post Rail Kit for use with P91(g)-1000, 1500, 2000, 3000; extends from 18.75" to 30.9"; packaging 3.8"W x 19.8"D x 2.8"H. 5 lbs. | 135
90000406 | XPC-2PRAIL | 2-Post Rail Kit for P80, P91(g) and NXRT 800VA thru 5kVA UPS or EBM; rated for 125 lbs; 4"W x 20"D x 3"H. 5 lbs. | 102
90000116 | XPC-2POSTL | 2-Post Shelf Kit for P91(g)-1000, 1500, 2000, 3000; rated for 150lbs; 21.5"W x 23.3"D x 3.5"H. 9 lbs. | 160
90001273 | XPC-2PRLV2 | 2-Post Shelf Kit with front ears for P91(g) Li; rated for 160lbs; 21.5"W x 23.3"D x 3.5"H. 9 lbs. | 225
90000392 | PV-WMB | Wall mount bracket for use with P80, P91(g) and P91L series UPSs and battery packs up to 5KVA; 4"W x 24"D x 4"H. 5 lbs. | 80
90000377 | P90-FRMB | Front Rackmount Bracket for P80 800VA through 2KVA size or P91 1KVA thru 2KVA size. Required when front mounting the UPS to a 2 post or 4 post rack with no rail kit. | 36
90000741 | SNMP-2PV3 | Internal SNMP/WEB Card for use with P80 or P91(g) Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-EMPV2 Environmental Monitor; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 359
90000674 | SNMP-EMPV2 | Environmental Monitoring Sensor to monitor room temperature and humidity - used with SNMP-2PV3 SNMP/WEB Card. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 230
90000267 | MODBUS-IN | MODBUS CARD for use with the P91(g) Series UPS; packaging = 7.25" x 6" x 2.5", 1 lbs | 319
90000265 | RELAY-MINI | Dry Contact RELAY CARD with DB9 & terminal block adapter; packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 120
90000090 | XBDM-1015LV | Xtreme Power XBDM Series 15 Amp Maintenance Bypass Distribution Module with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of BDM + (4) 5-15R output receptacles on rear of BDM; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads;3-Year Warranty (USA and Canada); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 379
90000091 | XBDM-1020LV | Xtreme Power XBDM Series 20 Amp Maintenance Bypass Distribution Module with 12' Input line cord with 5-20P plug; (6) 5-20R output receptacles on front of BDM + (4) 5-20R output receptacles on rear of BDM; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads; 3-Year Warranty (USA and Canada); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 419
90000093 | XBDM-1030LV | Xtreme Power XBDM Series 30 Amp Maintenance Bypass Distribution Module with 6' Input line cord with L5-30P plug; (5) 5-20R output receptacles on front of BDM (Load Group 1) + (5) 5-20R output receptacles on rear of BDM (Load Group 2); (2) bypass switches allowing for bypassing and maintenance of the UPS without affecting the connected loads; 3-Year Warranty (USA and Canada); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 659
90000041 | XPD1415HV | Xtreme Power XPDU Series Basic Power PDU with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of PDU + (8) 5-15R output receptacles on rear of PDU; UL60950-1/cUL/FCC Approved; 3-Year Warranty (USA and Canada); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 138
90000045 | XPD1420HV | Xtreme Power XPDU Series Basic Power PDU with 12' Input line cord with L5-20P plug (L5-20 to 5-20 adapter included); (6) 5-20R output receptacles on front of PDU + (8) 5-20R output receptacles on rear of PDU; UL60950-1/cUL/FCC Approved; 3-Year Warranty (USA and Canada); 19"W x 3.5"D x 1.75"H, 4.8 lbs | 190
90000094 | XBDM1020HV2 | Xtreme Power XBDM Series Maintenance Bypass Distribution Module with C20 input receptacle; rated at 16A; (2) IEC C19 and (4) IEC C13 output receptacles on front + (4) IEC C13 output receptacles on back; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads; Includes (2) IEC C20C19 cord kit; 3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 419
90000053 | XPDU-IEC | Xtreme Power XPDU Series Basic Power 230V PDU with C20 inlet (power cord ordered separately), (10) IEC C13 + (2) IEC C19 output receptacles; 1U Rackmount configuration; CE Listed; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 2.6 lbs | 190
90000269 | XAT-400 | 400VA Step Down Transformer, 208V to 120V for P90G and P90LG-3000. Input is 208V IEC C14 on 2ft cord; output is 120V 5-15R on 2ft cord. 7"W x 6.8"D x 5.9"H. 8 lbs. | 600
90000739 | XPD-IT15A | Xtreme Power XPDU Series PDU with Isolation Transformer. 1500W, 208V in, 120V out. IEC-C14 inlet with 3' 5-15 line cord ; (16) 5-15R output receptacles protected by 15A breaker; 3-Year Warranty; 17.5"W x 15"D x 3.5"H (2U), 43 lbs.. | 980
90001036 | P91ADVEX | Advanced Exchange Warranty Upgrade for advanced warranty exchange and shipping for P91(g)-1.5kLi, P91(g)-2kLi, and P91(g)-3kLi UPS (USA and Canada) | 250
P90L 1.5-3K Series Double Conversion UPS
90000912 | P90L-1500 | Xtreme Power P90L Series 1250VA/1125W; Online UPS; 2U; 120VAC; 6A charger w/ no internal batteries; 6' input line cord with 5-15 plug; (8) 5-15R output receptacles; Tower and rack mounting; 98% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; UL, cUL, RoHS approved; TAA Compliant; 3 year full Warranty (USA only); 50K load protection policy; 17.2" x 18.9" x 3.5"; 33 lbs | 1450
90000913 | P90L-2000 | Xtreme Power P90L Series 1700VA/1530W; Online UPS; 2U; 120VAC; 6A charger w/ no internal batteries; 6' input line cord with 5-20 plug; (8) 5-15/20R output receptacles; Tower and rack mounting; 98% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; UL, cUL, RoHS approved; TAA Compliant; 3 year full Warranty (USA only); 50K load protection policy; 17.2" x 18.9" x 3.5"; 35 lbs | 1675
90000914 | P90L-3000 | Xtreme Power P90L Series 2500VA/2250W; Online UPS; 2U; 120VAC; 6A charger w/ no internal batteries; 6' input line cord with L5-30 plug; (1) L5-30R + (4) 5-15/20R output receptacles; Tower and rack mounting; 98% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; UL, cUL, RoHS approved; TAA Compliant; 3 year full Warranty (USA only); 50K load protection policy; 17.2" x 25.8" x 3.5"; 47 lbs | 2525
90000921 | P90Lg-3000 | Xtreme Power P90L Series 3000VA/2400W; Online UPS; 2U; 208-240VAC; 6A charger w/ no internal batteries; IEC C20 to L6-20P detachable input line cord (8 ft); (1)IEC-C19 + (6) IEC-C13 output receptacles; Tower and rack mounting; 98% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; CE and RoHS approved; TAA Compliant; 3 year full Warranty (USA only); 50K load protection policy; 17.2" x 25.8" x 3.5"; 47 lbs | 2490
90000915 | P90-BP36 | Extended Runtime Battery Pack for use with P90/P90L-1500 (includes 6 each 12V9AH batteries); __ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower or Rack Mounting; TUV/UL, RoHS, cUL Approved; TAA Compliant; 3-Year Full Warranty (USA only); 17.2"W x 18.9"D x 3.5"H; 58.1 lbs | 920
90000923 | P90-BP36E | Extended Runtime Battery Pack for use with P90/P90L-1500 (includes 12 each 12V9AH batteries); __ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower or Rack Mounting; TUV/UL, RoHS, cUL Approved; TAA Compliant; 3-Year Full Warranty (USA only); 17.2"W x 23.6"D x 3.5"H; 104.4 lbs | 1320
90000916 | P90-BP48 | Extended Runtime Battery Pack for use with P80-1500, P80-2000, P90 and P90L-2000 UPSs; (includes 8 each 12V9AH batteries); __ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower or Rack Mounting; TUV/UL, RoHS, cUL Approved; TAA Compliant; 3-Year Full Warranty (USA only); 17.2"W x 18.9"D x 3.5"H; 74.6 lbs | 990
90000917 | P90-BP72 | Extended Runtime Battery Pack for use with P90/ P90L-3000 and P90g/P90Lg-3000 UPSs; (includes 12 each 12V9AH batteries) ;__ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower or Rack Mounting; TUV/UL, RoHS, cUL Approved; TAA Compliant; 3-Year Full Warranty (USA only); 17.2"W x 23.6"D x 3.5"H; 104.4 lbs | 1290
TBD | XPC-C14-615R | P91g Output Cord, 1ft, IEC C14 to 6-15R. 3 lbs. | 49
TBD | XPC-ZLC20-620R | Optional 12" output cord, Locking C20 to 6-15/20 receptacle for use with TX91; 3 lbs. | 79
TBD | XPC-ZLC20-L620R | Optional 12" output cord, Locking C20 to L6-20 receptacle for use with TX91; 3 lbs. | 79
TBD | XPC-ZLC20-L630R | Optional 12" output cord, Locking C20 to L6-30 receptacle for use with TX91; 3 lbs. | 79
90000909 | P90-RAIL | Adjustable Mounting 4-Post Rail Kit for P90L-1500/2000/3000 and P90-BP36/48/72; extends from 18.75" to 30.9"; packaging 3.8"W x 19.8"D x 2.8"H, 5 lbs | 135
90000406 | XPC-2PRAIL | 2-Post Rail Kit for P80, P90, P90L and NXRT 800VA thru 5kVA UPS or EBM; rated for 125 lbs; 4"W x 20"D x 3"H. 5 lbs. | 102
90000116 | XPC-2POSTL | 2-Post Shelf Kit for P90L-1500/2000/3000 and P90-BP36/48/72; 21/5"W x 23.3"D x 3.5"H. 9 lbs | 160
90000741 | SNMP-2PV3 | Internal SNMP/WEB Card for use with P80 or P90 Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-EMPv2 Environmental Monitor; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 359
90000674 | SNMP-EMPV2 | Environmental Monitoring Sensor to monitor room temperature and humidity - used with SNMP-2PV3 SNMP/WEB Card. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 230
90000265 | RELAY-MINI | Dry Contact RELAY CARD with DB9 & terminal block adapter; packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 120
90000267 | MODBUS-IN | MODBUS CARD for use with the P90L Series UPS; packaging = 7.25" x 6" x 2.5", 1 lbs | 319
90000090 | XBDM-1015LV | Xtreme Power XBDM Series 15 Amp Maintenance Bypass Distribution Module with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of BDM + (4) 5-15R output receptacles on rear of BDM; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads;3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 379
90000091 | XBDM-1020LV | Xtreme Power XBDM Series 20 Amp Maintenance Bypass Distribution Module with 12' Input line cord with 5-20P plug; (6) 5-20R output receptacles on front of BDM + (4) 5-20R output receptacles on rear of BDM; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads; 3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 419
90000093 | XBDM-1030LV | Xtreme Power XBDM Series 30 Amp Maintenance Bypass Distribution Module with 6' Input line cord with L5-30P plug; (5) 5-20R output receptacles on front of BDM (Load Group 1) + (5) 5-20R output receptacles on rear of BDM (Load Group 2); (2) bypass switches allowing for bypassing and maintenance of the UPS without affecting the connected loads; 3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 659
90000094 | XBDM1020HV2 | Xtreme Power XBDM Series Maintenance Bypass Distribution Module with C20 inlet for customer supplied power cord; rated at 16A; (2) IEC C19 and (4) IEC C13 output receptacles on front + (4) IEC C13 output receptacles on back; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads; Includes (2) IEC C20 to C19 cord kits for connecting the XBDM to the P90G-3000 or P90LG-3000 UPS; 3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 419
90000041 | XPD1415HV | Xtreme Power XPDU Series Basic Power PDU with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of PDU + (8) 5-15R output receptacles on rear of PDU; UL60950-1/cUL/FCC Approved; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 3.5 lbs | 138
90000045 | XPD1420HV | Xtreme Power XPDU Series Basic Power PDU with 12' Input line cord with L5-20P plug (L5-20 to 5-20 adapter included); (6) 5-20R output receptacles on front of PDU + (8) 5-20R output receptacles on rear of PDU; UL60950-1/cUL/FCC Approved; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 4.8 lbs | 190
90000053 | XPDU-IEC | Xtreme Power XPDU Series Basic Power 230V PDU with C20 inlet (power cord ordered separately), (10) IEC C13 + (2) IEC C19 output receptacles; 1U Rackmount configuration; CE Listed; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 2.6 lbs | 190
90000739 | XPD-IT15A | Xtreme Power XPDU Series PDU with Isolation Transformer. 1500W, 208V in, 120V out. IEC-C14 inlet with 3' 5-15 line cord ; (16) 5-15R output receptacles protected by 15A breaker; 3-Year Warranty; 17.5"W x 15"D x 3.5"H (2U), 43 lbs. | 980
90000269 | XAT-400 | 400VA Step Down Transformer, 208V to 120V for P90g and P90Lg-3000. Input is 208V IEC C14 on 2ft cord; output is 120V 5-15R on 2ft cord. 7"W x 6.8"D x 5.9"H. 8 lbs. | 600
90000527 | P90L5SP15 | Xtended 5YR Factory Warranty for P90L 1500VA (USA only) - 5 Year Coverage includes coverage of electronics, telephone technical support, advanced exchange and ground shipping both ways.. | 370
90000528 | P90L5SP23 | Xtended 5YR Factory Warranty for P90L 2000/3000VA and P90Lg-3000 (USA only) - 5 Year Coverage includes coverage of electronics, telephone technical support, advanced exchange and ground shipping both ways.. | 610
90000524 | P90L5SPBP | Xtended 5YR Factory Warranty for P90L-BP36/BP42/BP72 (USA only) - 5 Year Coverage includes coverage of battery pack, telephone technical support, advanced exchange and ground shipping both ways.. | 320
T91 Series Double Conversion 700VA-3KVA UPS
Part Number | MODEL | DESCRIPTION | LIST PRICE
90000480 | T91-700 | Xtreme Power T91 Series 700VA/700W Online UPS, 120VAC; 6' Input line cord with 5-15P plug; (6) 5-15R output receptacles; Full Load Runtime = 6 minutes; ECO Mode; 2A to 8A charger current adjustable by LCD; Tower; RS232/USB Port; Emergency Power Off (EPO); Includes USB Cable and ViewPower Software; UL/cUL/FCC/RoHS Approved; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada only); 5.6"W x 15.6"D x 8.6"H, 25.7 lbs; | 769
90000481 | T91-1000 | Xtreme Power T91 Series 1000VA/1000W Online UPS, 120VAC; 6' Input line cord with 5-15P plug; (6) 5-15R output receptacles; Full Load Runtime = 7 minutes; ECO Mode; 2A to 8A charger current adjustable by LCD; Tower; RS232/USB Port; Emergency Power Off (EPO); Includes Communications Cable and ViewPower Software; UL/cUL/FCC/RoHS Approved; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada only); 5.6"W x 15.6"D x 8.6"H, 30 lbs; | 949
90000482 | T91-1500 | Xtreme Power T91 Series 1500VA/1450W Online UPS, 120VAC; 6' Input line cord with 5-15P plug; (6) 5-15R output receptacles; Full Load Runtime = 3 minutes; ECO Mode; 2A to 8A charger current adjustable by LCD; Tower; RS232/USB Port; Emergency Power Off (EPO); Includes Communications Cable and ViewPower Software; UL/FCC/RoHS Approved; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA only); 5.6"W x 15.6"D x 8.6"H, 34.3 lbs; | 1149
90000483 | T91-2000 | Xtreme Power T91 Series 2000VA/1930W Online UPS, 120VAC; 6' Input line cord, L5-20P; (1) L5-20R and (8) 5-20R output receptacles; Full Load Runtime = 7 minutes; ECO Mode; 2A to 8A charger current adjustable by LCD; Tower; RS232/USB Port; Emergency Power Off (EPO); Includes Communications Cable and ViewPower Software; UL/cUL/FCC/RoHS Approved; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada only); 7.4"W x 16.5"D x 12.5"H, 63 lbs; | 1539
90001242 | T91-2000V2 | Xtreme Power T91 Series 2000VA/1930W Online UPS, 120VAC; 6' Input line cord, 5-20P; (1) L5-20R and (8) 5-20R output receptacles; Full Load Runtime = 7 minutes; ECO Mode; 2A to 8A charger current adjustable by LCD; Tower; RS232/USB Port; Emergency Power Off (EPO); Includes Communications Cable and ViewPower Software; UL/cUL/FCC/RoHS Approved; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada only); 7.4"W x 16.5"D x 12.5"H, 63 lbs; | 1539
90000485 | T91i-2000 | Xtreme Power T91i Series 2000VA/2000W Online UPS, 208-240VAC; IEC-C20 Inlet; (1) IEC-C19 and (8) IEC-C13 output receptacles; Full Load Runtime = 6 minutes; ECO Mode; 2A to 8A charger current adjustable by LCD; Tower; RS232/USB Port; Emergency Power Off (EPO); Includes USB Cable and ViewPower Software; CE, RoHS Approved; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada only); 7.4"W x 16.5"D x 12.5"H (190mmW x 421mmD x 318mmH) , 62 lbs; | 1629
90000484 | T91-3000 | Xtreme Power T91 Series 3000VA/2880W Online UPS, 120VAC; 6' Input line cord L5-30P; (1) L5-30R and (8) 5-15/20R output receptacles; Full Load Runtime = 3 minutes; ECO Mode; 2A to 8A charger current adjustable by LCD; Tower; RS232/USB Port; Emergency Power Off (EPO); Includes Communications Cable and ViewPower Software; UL/FCC/RoHS Approved; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada only); 7.4"W x 16.5"D x 12.5"H, 82 lbs; | 1979
90001214 | T91i-3000 | Xtreme Power T91i Series 3000VA/3000W Online UPS, 208/230VAC; IEC-C20 Inlet; (1) IEC-C19 and (8) IEC-C13 output receptacles; Full Load Runtime = 2 minutes; ECO Mode; 2A to 8A charger current adjustable by LCD; Tower; RS232/USB Port; Emergency Power Off (EPO); Includes USB Cable and ViewPower Software; CE, RoHS Approved; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada only); 7.4"W x 16.5"D x 12.5"H (190mmW x 421mmD x 318mmH) , 62 lbs; | 2149
90000486 | T91-BP36A | Extended Runtime Battery Pack (2 strings) for use with T91-1000, and T91-1500 (maximum 7 BP per UPS); __ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower; UL/FCC/RoHS Approved; TAA Compliant; 3-Year Battery Warranty (USA and Canada only); 5.6"W x 15.6"D x 8.6"H, 44 lbs | 699
90000487 | T91-BP72A | Extended Runtime Battery Pack (2 strings) for use with T91-2000, T91i-2000 and T91-3000 (maximum 7 BP per UPS); __ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower; UL/FCC/RoHS Approved; TAA Compliant; 3-Year Battery Warranty (USA and Canada only); 7.4"W x 16.5"D x 12.5"H, 82 lbs | 1259
90000741 | SNMP-2PV3 | Internal SNMP/WEB Card for use with P80 or P90 Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-EMPV2 Environmental Monitor; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 359
90000674 | SNMP-EMPV2 | Environmental Monitoring Sensor to monitor room temperature and humidity - used with SNMP-2PV3 SNMP/WEB Card. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 230
90000267 | MODBUS-IN | MODBUS CARD for use with the P90 Series UPS; packaging = 7.25" x 6" x 2.5", 1 lbs | 319
90000265 | RELAY-MINI | Dry Contact RELAY CARD with DB9 & terminal block adapter; packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 120
90000389 | T90-WMB | Wall mount bracket for use with T91-700 thru 1500 UPS. Compatible with any brick shaped UPS, between 4" and 8" wide. Rated for 40 lbs. 4.0" to 8.0 adjustable W x 7.0"D x 8.0"H. 5 lbs. | 219
90000269 | XAT-400 | 400VA Step Down Transformer, 208V to 120V for P90G and P90LG-3000. Input is 208V IEC C14 on 2ft cord; output is 120V 5-15R on 2ft cord. 7"W x 6.8"D x 5.9"H. 8 lbs. | 600
90000488 | T915SP715 | Xtended 5YR Factory Warranty for T91 1000/1500VA UPS (USA only) - 5 Year Coverage includes coverage of electronics and internal batteries, telephone technical support, advanced exchange and ground shipping both ways. | 350
90000489 | T915SP23 | Xtended 5YR Factory Warranty for T91 2000/3000VA UPS (USA only) - 5 Year Coverage includes coverage of electronics and internal batteries, telephone technical support, advanced exchange and ground shipping both ways. | 575
90000490 | T915SPBP | Xtended 5YR Factory Warranty for T91-BP1 and T91BP2 Extended Battery Packs (USA only) - 5 Year Coverage includes coverage of battery pack, telephone technical support, advanced exchange and ground shipping both ways. | 320
P91 SERIES 5, 6 & 10KVA 208/230V Bundled Solutions
Part Number | MODEL | DESCRIPTION | LIST PRICE
Bundle | P91-5KB | Xtreme Power P91- 5KVA/5KW online double conversion UPS in 4U total rack/tower configuration; 208-240VAC input and output; battery pack providing hot swappable battery trays and 7 minutes runtime at 5KW load; Terminal blocks for hardwired input and output; LCD display; intelligent slot for optional cards, RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 27.4"; Total Wt 163 lbs. Package Includes: P91-5k UPS Power Module (2U), BPXR2U240A Battery Module (2U), Tower Stands, Software; (2) 4 Post Rail Kits | 4658
Bundle | P91-5KB1 | Xtreme Power P91- 5KVA/5KW online double conversion UPS in 4U total rack/tower configuration; 208-240VAC input and output; Bypass distribution module, 2U battery pack providing hot swappable battery trays and 7 minutes runtime at 5KW load; input 6ft L6-30P line cord ; output (2) L6-30R, and (2) L6-20R receptacles; LCD display; intelligent slot for optional cards, RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 173 lbs. Package Includes: P91-5k UPS Power Module (2U), BPXR2U240A Battery Module (2U), XBDM-P91A Bypass PDU (0U) Tower Stands, Software; (2) 4 Post Rail Kits | 5546
Bundle | P91-5KB2 | Xtreme Power P91- 5KVA/5KW online double conversion UPS in 5U total rack/tower configuration; 208-240VAC input and output; battery pack providing hot swappable battery trays and 15 minutes runtime at 5KW load; Terminal blocks for hardwired input and output; LCD display; intelligent slot for optional cards, RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 27.4"; Total Wt 203 lbs. Package Includes: P91-5k UPS Power Module (2U), BPXR3U240A Battery Module (3U), Tower Stands, Software; (2) 4 Post Rail Kits | 5078
Bundle | P91-5KB3 | Xtreme Power P91- 5KVA/5KW online double conversion UPS in 5U total rack/tower configuration; 208-240VAC input and output; Bypass distribution module, 3U battery pack providing hot swappable battery trays and 15 minutes runtime at 5KW load; input 6ft L6-30P line cord ; output (2) L6-30R, and (2) L6-20R receptacles; LCD display; intelligent slot for optional cards, RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 213 lbs. Package Includes: P91-5k UPS Power Module (2U), BPXR3U240A Battery Module (3U), XBDM-P91A Bypass PDU (0U) Tower Stands, Software; (2) 4 Post Rail Kits | 5966
Bundle | P91-6KB | Xtreme Power P91- 6KVA/6KW online double conversion UPS in 4U total rack/tower configuration; 208-240VAC input and output; battery pack providing hot swappable battery trays and 5 minutes runtime at 6KW load; Terminal blocks for hardwired input and output; LCD display; intelligent slot for optional cards; RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 27.4"; Total Wt 164 lbs. Package Includes: P91-6k UPS Power Module (2U), BPXR2U240A Battery Module (2U), Tower Stands, Software; (2) 4 Post Rail Kits | 5048
Bundle | P91-6KB1 | Xtreme Power P91- 6KVA/6KW online double conversion UPS in 4U total rack/tower configuration; 208-240VAC input and output; Bypass distribution module, 2U battery pack providing hot swappable battery trays and 5 minutes runtime at 6KW load; input 6ft L6-30P line cord ; output (2) L6-30R, and (2) L6-20R receptacles; LCD display; intelligent slot for optional cards; RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 174 lbs. Package Includes: P91-6k UPS Power Module (2U), BPXR2U240A Battery Module (2U), XBDM-P91A Bypass PDU (0U) Tower Stands, Software; (2) 4 Post Rail Kits | 5936
Bundle | P91-6KB2 | Xtreme Power P91- 6KVA/6KW online double conversion UPS in 5U total rack/tower configuration; 208-240VAC input and output; battery pack providing hot swappable battery trays and 12 minutes runtime at 6KW load; Terminal blocks for hardwired input and output; LCD display; intelligent slot for optional cards; RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 27.4"; Total Wt 204 lbs. Package Includes: P91-6k UPS Power Module (2U), BPXR3U240A Battery Module (3U), Tower Stands, Software; (2) 4 Post Rail Kits | 5468
Bundle | P91-6KB3 | Xtreme Power P91- 6KVA/6KW online double conversion UPS in 5U total rack/tower configuration; 208-240VAC input and output; Bypass distribution module, 3U battery pack providing hot swappable battery trays and 12 minutes runtime at 6KW load; input 6ft L6-30P line cord ; output (2) L6-30R, and (2) L6-20R receptacles; LCD display; intelligent slot for optional cards; RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 214 lbs. Package Includes: P91-6k UPS Power Module (2U), BPXR3U240A Battery Module (3U), XBDM-P91A Bypass PDU (0U) Tower Stands, Software; (2) 4 Post Rail Kits | 6356
Bundle | P91-10KB | Xtreme Power P91- 10KVA/10KW online double conversion UPS in 5U total rack/tower configuration; 208-240VAC input and output; 3U battery pack providing hot swappable battery trays and 6 minutes runtime at 10KW load; Terminal blocks for hardwired input and output; LCD display; intelligent slot for optional cards; RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 27.4"; Total Wt 210 lbs. Package Includes: P91-10k UPS Power Module (2U), BPXR3U240A Battery Module (3U), Tower Stands, Software; (2) 4 Post Rail Kits | 6548
Bundle | P91-10KB1 | Xtreme Power P91- 10KVA/10KW online double conversion UPS in 5U total rack/tower configuration; 208-240VAC input and output; Bypass distribution module, 3U battery pack providing hot swappable battery trays and 6 minutes runtime at 10KW load; Hardwired Terminal Block input, output (1) L6-30R, (2) L6-20R receptacles and terminal blocks; LCD display; intelligent slot for optional cards; RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 218 lbs. Package Includes: P91-10k UPS Power Module (2U), BPXR3U240A Battery Module (3U), XBDM-P91B Bypass PDU (0U) Tower Stands, Software; (2) 4 Post Rail Kits | 7436
Bundle | P91-10KB2 | Xtreme Power P91- 10KVA/10KW online double conversion UPS in 4U total rack/tower configuration; 208-240VAC input and output; 2U battery pack providing hot swappable battery trays and 2 minutes runtime at 10KW load; Terminal blocks for hardwired input and output; LCD display; intelligent slot for optional cards; RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 27.4"; Total Wt 170 lbs. Package Includes: P91-10k UPS Power Module (2U), BPXR2U240A Battery Module (2U), Tower Stands, Software; (2) 4 Post Rail Kits | 6128
Bundle | P91-10KB3 | Xtreme Power P91- 10KVA/10KW online double conversion UPS in 4U total rack/tower configuration; 208-240VAC input and output; Bypass distribution module, 4U battery pack providing hot swappable battery trays and 2 minutes runtime at 10KW load; Hardwired Terminal Block input, output (1) L6-30R, (2) L6-20R receptacles and terminal blocks; LCD display; intelligent slot for optional cards; RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 178 lbs. Package Includes: P91-10k UPS Power Module (2U), BPXR2U240A Battery Module (2U), XBDM-P91B Bypass PDU (0U) Tower Stands, Software; (2) 4 Post Rail Kits | 7016
P91 SERIES 5, 6 & 10KVA 208-240 Input and 208/104 or 240/120V Output Bundled Solutions
Part Number | MODEL | DESCRIPTION | LIST PRICE
Bundle | P91-5KTB | Xtreme Power P91- 5KVA/5KW online double conversion UPS in 6U total rack/tower configuration; 208/240VAC input and 208/104V or 240/120V output; Bypass distribution module, 6kVA isolation transformer, battery pack providing hot swappable battery trays and 7 minutes runtime at 5KW load; input 6ft L6-30P line cord; output (2) L6-30R, (2) L6-20R and (12) 5-15/20R receptacles (6KW max 120V capability); LCD display; intelligent slot for optional cards, RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 315 lbs. Package Includes: P91-5k UPS Power Module (2U), BPXR2U240A Battery Module (2U), XBDM-P91A Bypass PDU (0U) (2) XPC-ZLC20-L6-20R XPD-IT60A Isolation Transformer (2U), Tower Stands, Software; (3) 4 Post Rail Kits | 7445
Bundle | P91-5KTB2 | Xtreme Power P91- 5KVA/5KW online double conversion UPS in 7U total rack/tower configuration; 208/240VAC input and 208/104V or 240/120V output; Bypass distribution module, 6kVA isolation transformer, battery pack providing hot swappable battery trays and 7 minutes runtime at 5KW load; input terminal block and 6ft L6-30P line cord; output Terminal block and (1) L6-30R, (2) L14-30R and (8) 5-15/20R receptacles; LCD display; intelligent slot for optional cards, RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 315 lbs. Package Includes: P91-5k UPS Power Module (2U), BPXR2U240A Battery Module (2U), XBDM-P91C Bypass PDU (0U) XPC-L630 Line Cord XPD-IT6KW Isolation Transformer (3U), Tower Stands, Software; (3) 4 Post Rail Kits | 7847
Bundle | P91-5KTB3 | Xtreme Power P91- 5KVA/5KW online double conversion UPS in 7U total rack/tower configuration; 208/240VAC input and 208/104V or 240/120V output; Bypass distribution module, 6kVA isolation transformer, battery pack providing hot swappable battery trays and 15 minutes runtime at 5KW load; input 6ft L6-30P line cord; output (2) L6-30R, (2) L6-20R and (12) 5-15/20R receptacles (6KW max 120V capability); LCD display; intelligent slot for optional cards, RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 355.1 lbs. Package Includes: P91-5k UPS Power Module (2U), BPXR3U240A Battery Module (3U), XBDM-P91A Bypass PDU (0U) (2) XPC-ZLC20-L6-20R XPD-IT60A Isolation Transformer (2U), Tower Stands, Software; (3) 4 Post Rail Kits | 7865
Bundle | P91-5KTB4 | Xtreme Power P91- 5KVA/5KW online double conversion UPS in 8U total rack/tower configuration; 208/240VAC input and 208/104V or 240/120V output; Bypass distribution module, 6kVA isolation transformer, battery pack providing hot swappable battery trays and 15 minutes runtime at 5KW load; input terminal block and 6ft L6-30P line cord; output Terminal block and (1) L6-30R, (2) L14-30R and (8) 5-15/20R receptacles ; LCD display; intelligent slot for optional cards, RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 355.1 lbs. Package Includes: P91-5k UPS Power Module (2U), BPXR3U240A Battery Module (3U), XBDM-P91C Bypass PDU (0U) XPC-L630 Line Cord XPD-IT6KW Isolation Transformer (3U), Tower Stands, Software; (3) 4 Post Rail Kits | 8267
Bundle | P91-6KTB | Xtreme Power P91- 6KVA/6KW online double conversion UPS in 6U total rack/tower configuration; 208/240VAC input and 208/104V or 240/120V output; Bypass distribution module, 6kVA isolation transformer, battery pack providing hot swappable battery trays and 5 minutes runtime at 6KW load; input 6ft L6-30P line cord; output (2) L6-30R, (2) L6-20R and (12) 5-15/20R receptacles (6KW max 120V capability); LCD display; intelligent slot for optional cards; RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 316 lbs. Package Includes: P91-6k UPS Power Module (2U), BPXR2U240A Battery Module (2U), XBDM-P91A Bypass PDU (0U) (2) XPC-ZLC20-L6-20R XPD-IT60A Isolation Transformer (2U), Tower Stands, Software; (3) 4 Post Rail Kits | 7835
Bundle | P91-6KTB2 | Xtreme Power P91- 6KVA/6KW online double conversion UPS in 7U total rack/tower configuration; 208/240VAC input and 208/120V or 240/120V output; Bypass distribution module, 6kVA isolation transformer, battery pack providing hot swappable battery trays and 5 minutes runtime at 6KW load; input terminal block and 6ft L6-30P line cord; output Terminal block and (1) L6-30R, (2) L14-30R and (8) 5-15/20R receptacles; LCD display; intelligent slot for optional cards, RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 316 lbs. Package Includes: P91-6k UPS Power Module (2U), BPXR2U240A Battery Module (2U), XBDM-P91C Bypass PDU (0U) XPC-L630 Line Cord XPD-IT6KW Isolation Transformer (3U), Tower Stands, Software; (3) 4 Post Rail Kits | 8237
Bundle | P91-6KTB3 | Xtreme Power P91- 6KVA/6KW online double conversion UPS in 7U total rack/tower configuration; 208/240VAC input and 208/104V or 240/120V output; Bypass distribution module, 6kVA isolation transformer, battery pack providing hot swappable battery trays and 12 minutes runtime at 6KW load; input 6ft L6-30P line cord; output (2) L6-30R, (2) L6-20R and (12) 5-15/20R receptacles (6KW max 120V capability); LCD display; intelligent slot for optional cards; RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 356 lbs. Package Includes: P91-6k UPS Power Module (2U), BPXR3U240A Battery Module (3U), XBDM-P91A Bypass PDU (0U) (2) XPC-ZLC20-L6-20R XPD-IT60A Isolation Transformer (2U), Tower Stands, Software; (3) 4 Post Rail Kits | 8255
Bundle | P91-6KTB4 | Xtreme Power P91- 6KVA/6KW online double conversion UPS in 8U total rack/tower configuration; 208/240VAC input and 208/120V or 240/120V output; Bypass distribution module, 6kVA isolation transformer, battery pack providing hot swappable battery trays and 12 minutes runtime at 6KW load; input terminal block and 6ft L6-30P line cord; output Terminal block and (1) L6-30R, (2) L14-30R and (8) 5-15/20R receptacles; LCD display; intelligent slot for optional cards, RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 356 lbs. Package Includes: P91-6k UPS Power Module (2U), BPXR3U240A Battery Module (3U), XBDM-P91C Bypass PDU (0U) XPC-L630 Line Cord XPD-IT6KW Isolation Transformer (3U), Tower Stands, Software; (3) 4 Post Rail Kits | 8675
Bundle | P91-10KTB | Xtreme Power P91- 10KVA/10KW online double conversion UPS in 7U total rack/tower configuration; 208/240VAC input and 208/104V or 240/120V output; Bypass distribution module, 6kVA isolation transformer, 3U battery pack providing hot swappable battery trays and 6 minutes runtime at 10KW load; hardwire terminal block input; output (1) L6-30R, (2) L6-20R and (12) 5-15/20R receptacles (6KW max 120V capability); LCD display; intelligent slot for optional cards; RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 360 lbs. Package Includes: P91-10k UPS Power Module (2U), BPXR3U240A Battery Module (3U), XBDM-P91B Bypass PDU (0U) XPD-IT60A Isolation Transformer (2U), Tower Stands, Software; (3) 4 Post Rail Kits | 9355
Bundle | P91-10KTB1 | Xtreme Power P91- 10KVA/10KW online double conversion UPS in 6U total rack/tower configuration; 208/240VAC input and 208/104V or 240/120V output; Bypass distribution module, 6kVA isolation transformer, 3U battery pack providing hot swappable battery trays and 2 minutes runtime at 10KW load; hardwire terminal block input; output (1) L6-30R, (2) L6-20R and (12) 5-15/20R receptacles (6KW max 120V capability); LCD display; intelligent slot for optional cards; RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 320 lbs. Package Includes: P91-10k UPS Power Module (2U), BPXR2U240A Battery Module (2U), XBDM-P91B Bypass PDU (0U) (2) C91 - L6-20R XPD-IT60A Isolation Transformer (2U), Tower Stands, Software; (3) 4 Post Rail Kits | 8901
Bundle | P91-10KTB2 | Xtreme Power P91- 10KVA/10KW online double conversion UPS in 8U total rack/tower configuration; 208/240VAC input and 208/104V or 240/120V output; Bypass distribution module, 10kW isolation transformer, 3U battery pack providing hot swappable battery trays and 6 minutes runtime at 10KW load; hardwire terminal block input; output terminal block and (1) L6-30R, (2) L14-30R and (8) 5-15/20R receptacles; LCD display; intelligent slot for optional cards; RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 49 lbs. Package Includes: P91-10k UPS Power Module (2U), BPXR3U240A Battery Module (3U), XBDM-P91C Bypass PDU (0U) XPD-IT10KW Isolation Transformer (3U), Tower Stands, Software; (3) 4 Post Rail Kits | 10187
P91 SERIES 5, 6 & 10KVA 208/230V Solutions
Part Number | MODEL | DESCRIPTION | LIST PRICE
90000640 | P91-5K | Xtreme Power P91 Series 5KVA/5kW Unity PF; Online UPS; 2U; 208VAC (selectable to 208, 220, 230 or 240); Input and Output connections are Terminal Block ; Set up for external batteries; adjustable 1-4 Amp 240V charger; Tower and rack mounting; 99% efficiency in ECO mode, Smart LCD screen; intelligent slot for optional cards, RS-232 and USB port connections; UL, cUL, FCC, RoHS approved; TAA Compliant; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 23.6"D x 3.5"H; 33.1 lbs. | 2310
90000641 | P91-6K | Xtreme Power P91 Series 6KVA/6kW Unity PF; Online UPS; 2U; 208VAC (selectable to 208, 220, 230 or 240); Input and Output connections are Terminal Block; Set up for external batteries; adjustable 1-4 Amp 240V charger; Tower and rack mounting; 99% efficiency in ECO mode, Smart LCD screen; intelligent slot for optional cards, RS-232 and USB port connections; UL, cUL, FCC, RoHS approved; TAA Compliant; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 23.6"D x 3.5"H; 34 lbs. | 2700
90000642 | P91-10K | Xtreme Power P91 Series 10KVA/10kW Unity PF; Online UPS; 2U; 208VAC (selectable to 208, 220, 230 or 240); Input and Output connections are Terminal Block; Set up for external batteries; adjusable 1-4 Amp 240V charger; Tower and rack mounting; 99% efficiency in ECO mode, intelligent slot for optional cards, Smart LCD screen; RS-232 and USB port connections; UL, cUL, FCC, RoHS approved; TAA Compliant; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 23.6"D x 3.5"H; 39.7 lbs. | 3780
90000643 | BPXR2U240A | Extended Runtime Battery Pack for use with P91- 5, 6 &10K UPSs; 2U; (includes 20 each 12V5AH batteries); Hot swappable internal battery trays; __ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower or Rack Mounting; Includes BP to UPS interconnection cable. TUV/UL, FCC, RoHS, cUL Approved; 3-Year Full Warranty (USA and Canada); 17.2"W x 27.4"D x 3.5"H; 120 lbs | 2050
90000644 | BPXR3U240A | Extended Runtime Battery Pack for use with P91-5, 6 &10K UPSs; 3U; (includes 20 each 12V580W batteries); Hot swappable internal battery trays; __ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower or Rack Mounting; Includes BP to UPS interconnection cable. TUV/UL, FCC, RoHS, cUL Approved; 3-Year Full Warranty (USA and Canada); 17.2"W x 27.4"D x 5.2"H; 160 lbs | 2470
90000645 | XBDM-P91A | XBDM, (Xtreme Bypass Distribution Module) for use with P91-5 & 6K UPSs; Input is L6-30P 6ft line cord; Outputs are (2) L6-30R and (2) C19 receptacles, breaker protected; Interconnection to and from UPS is via Anderson Connection cables and Cable for UPS static switch interlock(included). Includes Maintenance Bypass Switch; 0U, mounts to rear of battery pack or in rear of rack cabinet. 14.6"W x 5"D x 3.5"H. 8 lbs. | 730
| XBDM-P91A10 | XBDM, (Xtreme Bypass Distribution Module) for use with P91-5 & 6K UPSs; Input is L6-30P 10ft line cord; Outputs are (2) L6-30R and (2) C19 receptacles, breaker protected; Interconnection to and from UPS is via Anderson Connection cables and Cable for UPS static switch interlock(included). Includes Maintenance Bypass Switch; 0U, mounts to rear of battery pack or in rear of rack cabinet. 14.6"W x 5"D x 3.5"H. 8 lbs. | 760
90000646 | XBDM-P91B | XBDM, (Xtreme Bypass Distribution Module) for use with P91-5, 6 & 10K UPSs; Input is Terminal Block; Output is Terminal Block plus (1) L6-30R and (2) C19 receptacles, breaker protected; Interconnection to and from UPS is via Anderson Connection cables and Cable for UPS static switch interlock (included). Includes Maintenance Bypass Switch; 0U, mounts to rear of battery pack or in rear of rack cabinet; 14.6"W x 5"D x 3.5"H. 6 lbs. | 730
90000737 | XBDM-P91C | XBDM, (Xtreme Bypass Distribution Module) for use with P91-5, 6 & 10K UPSs; Input is Terminal Block; Output is Terminal Block plus (1) L6-30R, breaker protected; Interconnection to and from UPS is via Anderson Connection cables and Cable for UPS static switch interlock (included). Includes Maintenance Bypass Switch; 0U, mounts to rear of battery pack or in rear of rack cabinet. 14.6"W x 5"D x 3.5"H. 5lbs. | 730
90000738 | XBDM-P91D | XBDM, (Xtreme Bypass Distribution Module) for use with P91-5, 6 & 10K UPSs; Input is Terminal Block; Output is (2) L6-30R receptacles, breaker protected; Interconnection to and from UPS is via Anderson Connection cables and Cable for UPS static switch interlock(included). Includes Maintenance Bypass Switch; 0U, mounts to rear of battery pack or in rear of rack cabinet. 14.6"W x 5"D x 3.5"H. 6 lbs. | 730
| XPC-ZLC20-620R | Output Cord, 1ft, IEC Locking C20 to 6-15/20R for use with Xtreme Bypass Distribution Modules (XBDM) with C19 output. 1 lbs. | 79
| XPC-ZLC20-L620R | Output Cord,1ft, IEC Locking C20 to L6-20R for use with Xtreme Bypass Distribution Modules (XBDM) with C19 output. 1 lbs. | 79
| XPC-ZLC20-L630R | Output Cord, 1ft, IEC Locking C20 to L6-30R for use with Xtreme Bypass Distribution Modules (XBDM) with C19 output. 1 lbs. | 79
| XPC-C20-L615R | Output Cord, 1ft, IEC Non-locking C20 to L6-15R for use with Xtreme Bypass Distribution Modules (XBDM) with C19 output. 1 lbs. | 59
TBD | XPC-L630R | Optional L6-30R, 8" dongle style output receptacle for use with UPS with terminal block output; 12 lbs. | 125
TBD | XPC-L630P | Optional L6-30P line cord, 6ft line cord for use with 5 or 6K UPS with terminal block input; 12 lbs. | 125
90000407 | XPD-IT60A | Xtreme Power XPDU Series 6KVA PDU with Isolation Transformer for use with P80G-5000 or P91 5-10K UPS. 6000W, 208 or 240 in, 208/104V or 240/120V out. 3ft L6-30P Input Cord. (1) L6-30R and (12) 5-15-20R output receptacles; rear panel 208/240 voltage selection switch; includes front panel rackmount brackets; ROHS Approved; 3-Year Warranty; 17.3"W x 18"D x 3.5"H (2U), 137 lbs. | 1750
90000781 | XPD-IT6KW | 6kVA PDU with Isolation Transformer 208V to 240/120V (or 240V to 240/120V), Input terminal bock, Output terminal block + (2) L14-30R and (8) 5–15/20R receptacles; 17.3”W x 32.8”D x 5.2”H; 199 lbs. | 2310
90000740 | XPD-IT10KW | 10kVA PDU with Isolation Transformer 208V to 240/120V (or 240V to 240/120V), Input terminal bock, Output terminal block + (2) L14-30R and (8) 5–15/20R receptacles; 17.3”W x 32.8”D x 5.2”H; 209 lbs. | 2760
90000933 | P90L-RAIL | Adjustable Mounting 4-Post Rail Kit for P91 or P90L-5K, 6K, &10K UPS, BP & Transformer Module; extends from 21" to 35.5"; packaging = 3..8"W x 22"D x 2.8"H, 5 lbs | 149
90000116 | XPC-2POSTL | 2-Post Shelf Kit for P91 or P90L-5K, 6K, &10K UPS, BP & Transformer Module rated for 150lbs; 21/5"W x 23.3"D x 3.5"H. 9 lbs | 160
90003042 | XPC-2POST | Heavy Duty 2-Post Shelf Kit for P91 or P90L-5K, 6K, &10K UPS, BP & Transformer Module rated for 300lbs; 19"W x 29"D x 5.2"H. 14 lbs | 270
90000741 | SNMP-2PV3 | Internal SNMP/WEB Card for use with P80 or P90 Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-EMPV2 Environmental Monitor; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 359
90000674 | SNMP-EMPV2 | Environmental Monitoring Sensor to monitor room temperature and humidity - used with SNMP-2PV3 SNMP/WEB Card. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 230
90000267 | MODBUS-IN | MODBUS CARD for use with the P90L Series UPS; packaging = 7.25" x 6" x 2.5", 1 lbs | 319
90000265 | RELAY-MINI | Dry Contact RELAY CARD with DB9 & terminal block adapter; packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 120
90000374 | XPD24C13V | Xtreme Power XPDU Series Basic Power PDU, 30A, 200-240V; L6-30P 6ft line cord, (24) C13 output receptacles. Vertical Mount. 1.75"W x 1.75"D x 66"L. 12 lbs | 340
9000251 | XPD31 | Xtreme Power XPDU Series Basic Power PDU, 30A, 200-240V; L6-30P 6ft line cord, (2) L6-30R, (2) L6-20R and (4) 6-15/20R output receptacles. Rackmount. 19"W x 4.7"D x 3.5"H. 9 lbs | 580
90000252 | XPD32 | Xtreme Power XPDU Series Basic Power PDU, 30A, 200-240V; L6-30P 6ft line cord, (2) L6-30R, (4) L6-20R output receptacles. Rackmount. 19"W x 2.4"D x 3.5"H. 7.5 lbs | 580
90000253 | XPD33 | Xtreme Power XPDU Series Basic Power PDU, 30A, 200-240V; L6-30P 6ft line cord, (4) IEC-C19 and (8) IEC C13 output receptacle. s Rackmount. 19"W x 2.4"D x 3.5"H. 8 lbs | 450
90000254 | XPD34 | Xtreme Power XPDU Series Basic Power PDU, 30A, 240/120V; L14-30P 6ft line cord, (2) L6-30R, (4) L6-20R and (12) 5-20R output receptacles. Rackmount. 19"W x 4.7"D x 3.5"H. 9.5 lbs | 690
90000255 | XPD35 | Xtreme Power XPDU Series Basic Power PDU, 50A, 200-240V; Hardwire input with Pigtail, (2) L6-30R and (4) L6-20R output receptacles. Rackmount. 19"W x 2.4"D x 3.5"H. 7 lbs | 580
90000256 | XPD36 | Xtreme Power XPDU Series Basic Power PDU, 50A, 200-240V; Hardwired input with Pigtail, (4) IEC-C19 and (8) IEC C13 output receptacles. Rackmount. 19"W x 2.4"D x 3.5"H. 6.8 lbs | 460
P91 SERIES 5, 6 & 10KVA Service Plans
Part Number | MODEL | DESCRIPTION | LIST PRICE
90001282 | 9SUS8051 | P91 5x8 Startup and 1 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 3900
90001283 | 9SUS8052 | P91 5x8 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 4500
90001284 | 9USUS8053 | P91 5x8 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5100
90001285 | 9SU724051 | P91 7x24 Startup and 1 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5070
90001286 | 9SU724052 | P91 7x24 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5850
90001287 | 9SU724053 | P91 7x24 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioningof UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 6630
90000350 | P95P610 | Extended 5 Year Factory Warranty for P91-5K, P91-6K, and P91-10K | 1500
90001288 | 9PM58 | P91 Preventative Maintenance Service, 5x8. For Zone 1 (within 100 miles of XPC Service Center). | 3500
90001289 | 9PM724 | P91 Preventative Maintenance Service, 7x24. For Zone 1 (within 100 miles of XPC Service Center). | 4550
90000538 | SVCADD | Service adder for locations further than 100 miles. | 1050
90000355 | P9OS3BP | On-Site 3 Year service plan for BPXR2U240A and BPXR3U240A battery packs | 480
90000356 | P9OS5BP | On-Site 5 Year service plan for BPXR2U240A and BPXR3U240A battery packs | 1140
90000946 | P90L5SPBP2 | Extended 5 Year Factory Warranty for BPXR2U240A and BPXR3U240A battery packs | 700
TX91 Series Isolated Online UPS
TX91 3.8kVA UPS
90000579 | TX91-3.8K | Xtreme Power TX91 Series 3.8kVA/3.8kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; Full Load Runtime = 15 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 272 lbs. | 6350
90000572 | TX91-3.8KXR | Xtreme Power TX91 Series 3.8kVA/3.8kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; 580W batteries for Full Load Runtime = 21 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 275 lbs. | 8050
| TX91-3.8KB1#### | Xtreme Power TX91 Series 3.8kVA/3.8kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (6) Configurable 240V and (4) 5-15/20R output connections; (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Full Load Runtime = 15 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 277 lbs. | 7540
| TX91-3.8KXRB1#### | Xtreme Power TX91 Series 3.8kVA/3.8kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (6) Configurable 240V and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; 580W batteries for Full Load Runtime = 21 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 280 lbs. | 9240
| TX91-3.8KB2#### | Xtreme Power TX91 Series 3.8kVA/3.8kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (4) Configurable 240V, (1) L6-30R, and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Full Load Runtime = 15 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 277 lbs. | 7540
| TX91-3.8KXRB2#### | Xtreme Power TX91 Series 3.8kVA/3.8kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (4) Configurable 240V, (1) L6-30R, and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; 580W batteries for Full Load Runtime = 21 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 280 lbs. | 9240
90000587 | TX91L-3.8K | Xtreme Power TX91L Series 3.8kVA/3.8kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; Set up for external batteries; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 152 lbs. External batteries to be ordered seperately. | 5100
| TX91L-3.8KB1#### | Xtreme Power TX91L Series 3.8kVA/3.8kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (6) Configurable 240V and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R. D = (1) L6-15R; Set up for external batteries; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 157 lbs. External batteries to be ordered seperately. | 6290
| TX91L-3.8KB2#### | Xtreme Power TX91L Series 3.8kVA/3.8kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (4) Configurable 240V, (1) L6-30R, and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Set up for external batteries; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 157 lbs. External batteries to be ordered seperately. | 6290
TX91 5kVA UPS
90000573 | TX91-5K | Xtreme Power TX91 Series 5kVA/5kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; Full Load Runtime = 10 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 275 lbs. | 7200
90000574 | TX91-5KXR | Xtreme Power TX91 Series 5kVA/5kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; 580W batteries for Full Load Runtime = 15 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 278 lbs. | 8900
| TX91-5KB1#### | Xtreme Power TX91 Series 5kVA/5kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (6) Configurable 240V and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Full Load Runtime = 10 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 280 lbs. | 8390
| TX91-5KXRB1#### | Xtreme Power TX91 Series 5kVA/5kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (6) Configurable 240V and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; 580W batteries for Full Load Runtime = 15 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 283 lbs. | 10090
| TX91-5KB2#### | Xtreme Power TX91 Series 5kVA/5kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (4) Configurable 240V, (1) L6-30R and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Full Load Runtime = 10 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 280 lbs. | 8390
| TX91-5KXRB2#### | Xtreme Power TX91 Series 5kVA/5kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (4) Configurable 240V, (1) L6-30R and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; 580W batteries for Full Load Runtime = 15 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 283 lbs. | 10090
90000588 | TX91L-5K | Xtreme Power TX91L Series 5kVA/5kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; Set up for external batteries; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 155 lbs. External batteries to be ordered seperately. | 6050
| TX91L-5KB1#### | Xtreme Power TX91L Series 5kVA/5kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (6) Configurable 240V and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Set up for external batteries; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 160 lbs. External batteries to be ordered seperately. | 7240
| TX91L-5KB2#### | Xtreme Power TX91L Series 5kVA/5kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (4) Configurable 240V, (1) L6-30R and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Set up for external batteries; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 160 lbs. External batteries to be ordered seperately. | 7240
TX91 6kVA UPS
90000575 | TX91-6K | Xtreme Power TX91 Series 6kVA/6kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; Full Load Runtime = 8 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 278 lbs. | 8050
90000576 | TX91-6KXR | Xtreme Power TX91 Series 6kVA/6kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; 580W batteries for Full Load Runtime = 12 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 281 lbs. | 9750
| TX91-6KB1#### | Xtreme Power TX91 Series 6kVA/6kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (6) Configurable 240V and (4) 5-15/20R output connections; (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Full Load Runtime = 8 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 283 lbs. | 9240
| TX91-6KXRB1#### | Xtreme Power TX91 Series 6kVA/6kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (6) Configurable 240V and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; 580W batteries for Full Load Runtime = 12 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 286 lbs. | 10940
| TX91-6KB2#### | Xtreme Power TX91 Series 6kVA/6kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (4) Configurable 240V, (1) L6-30R, and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Full Load Runtime = 8 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 277 lbs. | 9240
| TX91-6KXRB2#### | Xtreme Power TX91 Series 6kVA/6kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (4) Configurable 240V, (1) L6-30R, and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; 580W batteries for Full Load Runtime = 12 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 286 lbs. | 10940
90000589 | TX91L-6K | Xtreme Power TX91L Series 6kVA/6kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; Set up for external batteries; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 158 lbs. External batteries to be ordered seperately. | 6800
| TX91L-6KB1#### | Xtreme Power TX91L Series 6kVA/6kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (6) Configurable 240V and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Set up for external batteries; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 163 lbs. External batteries to be ordered seperately. | 7990
| TX91L-6KB2#### | Xtreme Power TX91L Series 6kVA/6kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (4) Configurable 240V, (1) L6-30R, and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Set up for external batteries; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 163 lbs. External batteries to be ordered seperately. | 7990
TX91 10kVA UPS
90000577 | TX91-10K | Xtreme Power TX91 Series 10kVA/10kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; Full Load Runtime = 3 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 307 lbs. | 11340
90000574 | TX91-10KXR | Xtreme Power TX91 Series 10kVA/10kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; 580W batteries for Full Load Runtime = 6 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; 3-Year Electronics, TAA Compliant; 3-Year Battery Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 310 lbs. | 12900
| TX91-10KB1#### | Xtreme Power TX91 Series 10kVA/10kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and (6) Configurable 240V and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Full Load Runtime = 3 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 312 lbs. | 12530
| TX91-10KXRB1#### | Xtreme Power TX91 Series 10kVA/10kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and (6) Configurable 240V and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; 580W batteries for Full Load Runtime = 6 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 315 lbs. | 14090
| TX91-10KB2#### | Xtreme Power TX91 Series 10kVA/10kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and (4) Configurable 240V, (1) L6-30R and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Full Load Runtime = 3 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 312 lbs. | 12530
| TX91-10KXRB2#### | Xtreme Power TX91 Series 10kVA/10kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and (4) Configurable 240V, (1) L6-30R and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; 580W batteries for Full Load Runtime = 6 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 315 lbs. | 14090
90000588 | TX91L-10K | Xtreme Power TX91L Series 10kVA/10kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; Set up for external batteries; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 187 lbs. External batteries to be ordered seperately. | 9240
| TX91L-10KB1#### | Xtreme Power TX91L Series 10kVA/10kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and (6) Configurable 240V and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Set up for external batteries; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 192 lbs. External batteries to be ordered seperately. | 10430
| TX91L-10KB2#### | Xtreme Power TX91L Series 10kVA/10kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and (4) Configurable 240V, (1) L6-30R and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Set up for external batteries; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 192 lbs. External batteries to be ordered seperately. | 10430
TX91 Battery Options
Part Number | Model | Description | List Price
90000584 | TX91-BP960-1 | External Battery Pack Module for TX91 3.8 - 10kVA UPS, Contains 1 String of batteries (20), Up to three battery packs per UPS can be used for extended runtime applications; __ Battery Packs provide(s) __ minutes runtime @ __KVA load., 9.8"W x 22.3"D x 32.4"H, 190 lbs | 3400
90000585 | TX91-BP960-2 | External Battery Pack Module for TX91 3.8 - 10kVA UPS, Contains 2 Strings of batteries (40), Up to three battery packs per UPS can be used for extended runtime applications; __ Battery Packs provide(s) __ minutes runtime @ __KVA load., 9.8"W x 22.3"D x 32.4"H, 320 lbs | 4900
90000586 | TX91-BP960-3 | External Battery Pack Module for TX91 3.8 - 10kVA UPS, Contains 3 Strings of batteries (60), Up to three battery packs per UPS can be used for extended runtime applications; __ Battery Packs provide(s) __ minutes runtime @ __KVA load., 9.8"W x 22.3"D x 32.4"H, 450 lbs | 6450
90000762 | TX91-CHG | TX91 External Battery Charger. Rated at 240VDC, 8A output with output cable to plug into TX91-BP960-x battery pack. Input rated at 208-240 VAC, 10A hardwired input. | 780
TX91 External Bypass Switch Options
| 90885-C241310ECA050A05013MB | Three-Breaker Maintenance Bypass Switch; 240VAC, Single-Phase, 50 A, 10kAIC; rated for up to 8KVA; Wallmount; includes UPS Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker,interlock plate, lockable front panel, UL981, Black. 22"W x 24"H x 9"D; 55 lbs. | Call for Price
| 90885-C241310ECA070A07013MB | Three-Breaker Maintenance Bypass Switch; 240VAC, Single-Phase, 70 A, 10kAIC; rated for up to 12KVA; Wallmount; includes UPS Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker,interlock plate, lockable front panel, UL981, Black. 22"W x 24"H x 9"D; 55 lbs. | Call for Price
TX91 Output Cords
Part Number | Model | Description | List Price
| XPC-ZLC20-620R | Optional 12" output cord, Locking C20 to 6-15/20 receptacle for use with TX91; 3 lbs. | 79
| XPC-ZLC20-L620R | Optional 12" output cord, Locking C20 to L6-20 receptacle for use with TX91; 3 lbs. | 79
| XPC-ZLC20-L630R | Optional 12" output cord, Locking C20 to L6-30 receptacle for use with TX91; 3 lbs. | 79
| XPC-C20-L615R | Optional 12" output cord. Non-locking C20 to L6-15 receptacle for use with TX91; 3 lbs | 59
TBD | XPC-L630R | Optional L6-30R, 8" dongle style output receptacle for use with UPS with terminal block output; 12 lbs. | 125
TBD | XPC-L630P | Optional L6-30P line cord, 6ft line cord for use with 5 or 6K UPS with terminal block input; 12 lbs. | 125
TBD | XPC-L1430R | Optional L14-30R, 8" dongle style output receptacle for use with TX90-6K; 12 lbs. | 125
TX91 Distribution Options
Part Number | Model | Description | List Price
90000251 | XPD31 | Xtreme Power XPDU Series Basic Power PDU for use with TX91-3.8KVA - 10KVA UPS, 30A, 200-240V; L6-30P 6ft line cord, (2) L6-30R, (2) L6-20R and (4) 6-15/20R output receptacles. Rackmount. 19"W x 4.7"D x 3.5"H. 9 lbs | 580
90000252 | XPD32 | Xtreme Power XPDU Series Basic Power PDU for use with TX91-3.8KVA - 10KVA UPS, 30A, 200-240V; L6-30P 6ft line cord, (2) L6-30R, (4) L6-20R output receptacles. Rackmount. 19"W x 2.4"D x 3.5"H. 7.5 lbs | 580
90000253 | XPD33 | Xtreme Power XPDU Series Basic Power PDU for use with TX91-3.8KVA - 10KVA UPS, 30A, 200-240V; L6-30P 6ft line cord, (4) IEC-C19 and (8) IEC C13 output receptacle. s Rackmount. 19"W x 2.4"D x 3.5"H. 8 lbs | 450
90000254 | XPD34 | Xtreme Power XPDU Series Basic Power PDU, 30A, 240/120V; L14-30P 6ft line cord, (2) L6-30R, (4) L6-20R and (12) 5-20R output receptacles. Rackmount. 19"W x 4.7"D x 3.5"H. 9.5 lbs | 690
90001037 | XPD38 | Xtreme Power XPDU Series Basic Power PDU, 30A, 120V; L14-30P, 6' input cord , (4) L5-30R, (4) L5-20R output receptacles. Rackmount. 19"W x 4.7"D x 3.5"H. 9.5 lbs | 690
TX91 Communication Options
Part Number | Model | Description | List Price
90000741 | SNMP-2PV3 | Internal SNMP/WEB Card for use with TX91 Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-EMPV2 Environmental Monitor; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 359
90000674 | SNMP-EMPV2 | Environmental Monitoring Sensor to monitor room temperature and humidity - used with SNMP-2PV3 SNMP/WEB Card. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 230
90000267 | MODBUS-IN | MODBUS CARD for use with the TX91 Series UPS; packaging = 7.25" x 6" x 2.5", 1 lbs | 319
90000265 | RELAY-MINI | Dry Contact RELAY CARD with DB9 & terminal block adapter; packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 120
TX91 Warranty and Service Options
Part Number | Model | Description | List Price
90001282 | 9SUS8051 | M90S 5x8 Startup and 1 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 3900
90001283 | 9SUS8052 | M90S 5x8 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 4500
90001284 | 9USUS8053 | M90S 5x8 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5100
90001285 | 9SU724051 | M90S 7x24 Startup and 1 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5070
90001286 | 9SU724052 | M90S 7x24 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5850
90001287 | 9SU724053 | M90S 7x24 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioningof UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 6630
90001288 | 9PM58 | M90S Preventative Maintenance Service, 5x8. For Zone 1 (within 100 miles of XPC Service Center). | 3500
90001289 | 9PM724 | M90S Preventative Maintenance Service, 7x24. For Zone 1 (within 100 miles of XPC Service Center). | 4550
90000538 | SVCADD | Service adder for locations further than 100 miles. | 1050
90000375 | T9VCNFG | Non-Standard Voltage Configuration adder. Required when setting the TX91 (XR), TX91L, or TXVR input voltage to 200V, 230V, or 240V. Input Voltage: Output Voltage on-line/inverter: Output Voltage on Bypass: Displayed Voltage: | 300
TXVR Voltage Regulator 3.8kVA - 10kVA
Part Number | Model | Description | List Price
90000494 | TXVR-3.8K | Xtreme Power TXVR Series 3.8kVA/3.8kW Isolated Electronic Voltage Regulator, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; Isolation transformer; regulates voltage to within +/- 1%; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL, cUL, RoHS Listed; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 142 lbs. | 4260
| TXVR-3.8KB1#### | Xtreme Power TXVR Series 3.8kVA/3.8kW Isolated Electronic Voltage Regulator, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (6) Configurable 240V and (4) 5-15/20R output connections; (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Isolation transformer; regulates voltage to within +/- 1%; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 147 lbs. | 5810
| TXVR-3.8KB2#### | Xtreme Power TXVR Series 3.8kVA/3.8kW Isolated Electronic Voltage Regulator, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (4) Configurable 240V, (1) L6-30R, and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Isolation transformer; regulates voltage to within +/- 1%; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 147 lbs. | 5810
TXVR 5kVA Voltage Regulator
90000495 | TXVR-5K | Xtreme Power TXVR Series 5kVA/5kW Isolated Electronic Voltage Regulator, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; Isolation transformer; regulates voltage to within +/- 1%; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 145 lbs. | 5900
| TXVR-5KB1#### | Xtreme Power TXVR Series 5kVA/5kW Isolated Electronic Voltage Regulator, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (6) Configurable 240V and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Isolation transformer; regulates voltage to within +/- 1%; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 150 lbs. | 7090
| TXVR-5KB2#### | Xtreme Power TXVR Series 5kVA/5kW Isolated Electronic Voltage Regulator, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (4) Configurable 240V, (1) L6-30R and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Isolation transformer; regulates voltage to within +/- 1%; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 150 lbs. | 7090
TXVR 6kVA Voltage Regulator
90000496 | TXVR-6K | Xtreme Power TXVR Series 6kVA/6kW Isolated Electronic Voltage Regulator, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; Isolation transformer; regulates voltage to within +/- 1%; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 148 lbs. | 6250
| TXVR-6KB1#### | Xtreme Power TXVR Series 6kVA/6kW Isolated Electronic Voltage Regulator, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (6) Configurable 240V and (4) 5-15/20R output connections; (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Isolation transformer; regulates voltage to within +/- 1%; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 153 lbs. | 7440
| TXVR-6KB2#### | Xtreme Power TXVR Series 6kVA/6kW Isolated Electronic Voltage Regulator, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (4) Configurable 240V, (1) L6-30R, and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Isolation transformer; regulates voltage to within +/- 1%; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 153 lbs. | 7440
TXVR 10kVA Voltage Regulator
90000497 | TXVR-10K | Xtreme Power TXVR Series 10kVA/10kW Isolated Electronic Voltage Regulator, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; Isolation transformer; regulates voltage to within +/- 1%; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 187 lbs. | 8710
| TXVR-10KB1#### | Xtreme Power TXVR Series 10kVA/10kW Isolated Electronic Voltage Regulator, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and (6) Configurable 240V and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Isolation transformer; regulates voltage to within +/- 1%; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 192 lbs. | 9905
| TXVR10KB2#### | Xtreme Power TXVR Series 10kVA/10kW Isolated Electronic Voltage Regulator, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and (4) Configurable 240V, (1) L6-30R and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Isolation transformer; regulates voltage to within +/- 1%; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 192 lbs. | 9905
TX91 Output Cords
Part Number | Model | Description | List Price
| XPC-ZLC20-620R | Optional 12" output cord, Locking C20 to 6-15/20 receptacle for use with TXVR; 3 lbs. | 79
| XPC-ZLC20-L620R | Optional 12" output cord, Locking C20 to L6-20 receptacle for use with TXVR; 3 lbs. | 79
| XPC-ZLC20-L630R | Optional 12" output cord, Locking C20 to L6-30 receptacle for use with TXVR; 3 lbs. | 79
| XPC-C20-L615R | Optional 12" output cord. Non-locking C20 to L6-15 receptacle for use with TX91; 3 lbs | 59
TBD | XPC-L630P | Optional L6-30P line cord, 6ft line cord for use with T90-6K or TX90-6K; 12 lbs. | 125
TBD | XPC-L630R | Optional L6-30R, 8" dongle style output receptacle for use with T90-6K or TX90-6K; 12 lbs. | 125
TBD | XPC-L1430R | Optional L14-30R, 8" dongle style output receptacle for use with TX90-6K; 12 lbs. | 125
TX91 Distribution Options
Part Number | Model | Description | List Price
90000251 | XPD31 | Xtreme Power XPDU Series Basic Power PDU for use with TXVR Series, 30A, 200-240V; L6-30P 6ft line cord, (2) L6-30R, (2) L6-20R and (4) 6-15/20R output receptacles. Rackmount. 19"W x 4.7"D x 3.5"H. 9 lbs | 580
90000252 | XPD32 | Xtreme Power XPDU Series Basic Power PDU for use with TXVR Series, 30A, 200-240V; L6-30P 6ft line cord, (2) L6-30R, (4) L6-20R output receptacles. Rackmount. 19"W x 2.4"D x 3.5"H. 7.5 lbs | 580
90000253 | XPD33 | Xtreme Power XPDU Series Basic Power PDU for use with TXVR Series, 30A, 200-240V; L6-30P 6ft line cord, (4) IEC-C19 and (8) IEC C13 output receptacle. s Rackmount. 19"W x 2.4"D x 3.5"H. 8 lbs | 450
90000254 | XPD34 | Xtreme Power XPDU Series Basic Power PDU, 30A, 240/120V; L14-30P 6ft line cord, (2) L6-30R, (4) L6-20R and (12) 5-20R output receptacles. Rackmount. 19"W x 4.7"D x 3.5"H. 9.5 lbs | 690
90001037 | XPD38 | Xtreme Power XPDU Series Basic Power PDU, 30A, 120V; L14-30P, 6' input cord , (4) L5-30R, (4) L5-20R output receptacles. Rackmount. 19"W x 4.7"D x 3.5"H. 9.5 lbs | 690
TX91 Communication Options
Part Number | Model | Description | List Price
90000741 | SNMP-2PV3 | Internal SNMP/WEB Card for use with TXVR Series; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-EMPV2 Environmental Monitor; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 359
90000674 | SNMP-EMPV2 | Environmental Monitoring Sensor to monitor room temperature and humidity - Must be used with SNMP-2PV3 SNMP/WEB Card. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 230
90000267 | MODBUS-IN | MODBUS CARD for use with the TXVR Series UPS; packaging = 7.25" x 6" x 2.5", 1 lbs | 319
90000265 | RELAY-MINI | Dry Contact RELAY CARD with DB9 & terminal block adapter; packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 120
TX91 Warranty and Service Options
Part Number | Model | Description | List Price
90001282 | 9SUS8051 | M90S 5x8 Startup and 1 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 3900
90001283 | 9SUS8052 | M90S 5x8 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 4500
90001284 | 9USUS8053 | M90S 5x8 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5100
90001285 | 9SU724051 | M90S 7x24 Startup and 1 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5070
90001286 | 9SU724052 | M90S 7x24 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5850
90001287 | 9SU724053 | M90S 7x24 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioningof UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 6630
90001288 | 9PM58 | M90S Preventative Maintenance Service, 5x8. For Zone 1 (within 100 miles of XPC Service Center). | 3500
90001289 | 9PM724 | M90S Preventative Maintenance Service, 7x24. For Zone 1 (within 100 miles of XPC Service Center). | 4550
90000538 | SVCADD | Service adder for locations further than 100 miles. | 1050
90000375 | T9VCNFG | Non-Standard Voltage Configuration adder. Required when setting the TX91 (XR), TX91L, or TXVR input voltage to 200V, 230V, or 240V. Input Voltage: Output Voltage on-line/inverter: Output Voltage on Bypass: Displayed Voltage: | 300
M90S Series Modular Double Conversion Split-Phase
M90S Series Ala Carte Solutions
Part Number | Model | Description | List Price
90000690 | M90S-ENC2 | XPC M90S 2-slot enclosure; Up to 6kVA/6kW; On Line - Rack Mount configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Integral Rear Mounted Maintenance Bypass switch, RS-232, USB, dry contacts, EPO, intelligent slot for optional card (Web/SNMP, Relay, Modbus); Communication Software and Cable; UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Power Module and Battery Module purchased separately; Unit Dims: 17.4"W X 33.7"D x 10.5"H. Weight: 38 lbs. | 1800
90000691 | M90S-ENC4 | XPC M90S 4-slot enclosure; Up to 12kVA/12kW; On Line - Tower configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Integral Front Access Maintenance Bypass switch, Floor mount bracket; Communications Module; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable; UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Power Modules, Battery Modules, and Blank Panels purchased separately; Dims: 17.4"W X 33.7"D x 33"H. Weight: 150 lbs. | 4800
90000692 | M90S-ENC6 | XPC M90S 6-slot enclosure; Up to 24kVA/24kW; On Line - Tower configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Integral Front Access Maintenance Bypass switch, Floor mount bracket; Communications Module; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus) Communication Software and Cable; UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Power Modules, Battery Modules, and Blank Panels purchased separately; Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 180 lbs. | 7250
90000693 | M90S-PWM6 | 6KVA/6KW Power Module for XPC M90S UPS; On Line- 120/208V In-120/208V Out or 120/240V In - 120/240V Out; LCD Screen, Dims: 16.3"W X 24"D x 5.2"H (3U). Weight: 38 lbs. | 4190
90001262 | M90S-BMXRV2 | Battery Module for XPC M90S UPS; Contains two battery sleeves, each containing (8) 12V 580W batteries; battery breaker; 16.3"W X 24"D x 5.2"H. Weight: 107 lbs. Note: Minimum of one battery module required for each power module used for capacity. | 2095
90000696 | M90S-BC7 | XPC M90S External Battery Enclosure; 7-slot enclosure holds up to (7) M90S-BMXR battery modules; Includes Casters. Battery Modules and Blank Panels purchased separately; Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 162 lbs. | 4935
90000717 | XPC-L14-30P | L14-30P input cord, 8 ft, (6KVA UPS only). Limits current to 24A continuous input current. | 135
90000719 | M90S-CB | Caster Base for M90S-ENC2. Locking casters. Dims: 17"W X 24"D x 4.0"H. Weight: 15 lbs. | 610
90000703 | M90S-BP | M90S Matching Blank Panel covers front of unused slots. Dims: 16.5"W X 2"D x 5.2"H. Weight: 5 lbs. | 63
90000695 | M90S-RAIL2S | M90S Rail Kit for M90S-ENC2 2-slot enclosure. Dims: 20"W X 4"D x 2.5"H. Weight: 5 lbs. | 155
90001332 | M90S-RMK | Rack mount kit to mount M90S-4S, M90S-6S, M90C-6S, M90Ci-6S, or M90S-BC7 enclosures into the bottom of a 19" rack. Includes: Ramp, Shelf, ann Front Mounting Ears | 680
| M90S4S-SEIS | Seismic Hold Down Achorage for M90S-ENC4 enclosure. Includes calculations with State of California Engineer Stamp. | 1900
| M90S6S-SEIS | Seismic Hold Down Achorage for M90S-ENC6 enclosure. Includes calculations with State of California Engineer Stamp. | 1900
M90S Series Optional Receptacle Panels (6S = up to 4 RP) (4S = up to 2 RP), (2S = up to 1 RP)
Part Number | Model | Description | List Price
90000699 | M90S-RPA | XPC M90S Optional Receptacle Panel. Contains (8) 5-20R receptacles. Mounts to rear of UPS Chassis. Weight: 5 lbs. | 295
90000700 | M90S-RPB | XPC M90S Optional Receptacle Panel. Contains (2) C19 and (4) 5-20R receptacles. Mounts to rear of UPS Chassis. Weight: 5 lbs. | 295
90000701 | M90S-RPC | XPC M90S Optional Receptacle Panel. Contains (1) L6-30R and (2) C19 receptacles. Mounts to rear of UPS Chassis. Weight: 5 lbs. | 295
90000703 | M90S-RPD | XPC M90S Optional Receptacle Panel. Contains (1) L14-30R and (2) C19 receptacles. Mounts to rear of UPS Chassis. Weight: 5 lbs. | 295
Bundle | M90S-RPE | XPC M90S Optional Receptacle Panel. Contains (2) L6-20R and (4) 5-20R receptacles. Mounts to rear of UPS Chassis. Weight: 5 lbs. | 453
Bundle | M90S-RPF | XPC M90S Optional Receptacle Panel. Contains (1) L6-30R, (1) L6-20R and (4) 5-20R receptacles. Mounts to rear of UPS Chassis. L6-30R protected by 20A breaker; Weight: 5 lbs. | 453
Bundle | M90S-RPG | XPC M90S Optional Receptacle Panel. Contains (1) L6-30R and (2) L6-20R receptacles. Mounts to rear of UPS Chassis. Weight: 5 lbs. | 453
Bundle | M90S-RPH | XPC M90S Optional Receptacle Panel. Contains (3) L6-30R receptacles. Mounts to rear of UPS Chassis. (2) L6-30R protected by 20A breakers; Weight: 5 lbs. | 453
M90S Series Hardwired Bundled Solutions
M90S 2-Slot 6KVA RM Hardwired Bundled Solutions
Part Number | Model | Description | List Price
Bundle | M90S-2S6K | XPC M90S UPS bundle; 6kVA/6kW; On Line-Rackmount Configuration,120/208V In/Out or 120/240V In/Out, Hardwired in/out. Bundle includes M90S-ENC2 2-Slot Enclosure with Integral Maintenance Bypass, Rackmount rails; (1) Power Module and (1) Battery Module providing 9 minutes runtime @ 6KVA/6KW load; RS-232, USB, dry contacts, EPO, intelligent slot for optional card (Web/SNMP, Relay, Modbus; ) Communication Software and Cable; UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 16.3"W X 24"D x 10.5"H. Weight: 185 lbs. | 8240
Bundle | M90S-2S6KT | XPC M90S UPS bundle; 6kVA/6kW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out. Bundle includes M90S-ENC2 2-Slot Enclosure with Integral Maintenance Bypass; Caster Base, (1) Power Module and (1) Battery Module providing 9 minutes runtime @ 6KVA/6KW load; RS-232, USB, dry contacts, EPO, intelligent slot for optional card (Web/SNMP, Relay, Modbus) Communication Software and Cable; UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, Battery Module and Caster Base shipped seperately. Dims: 17"W X 24"D x 14.5"H. Weight: 198 lbs. | 8695
M90S 4-Slot 6KVA Hardwired Bundled Solutions
Part Number | Model | Description | List Price
| M90S-4S6K1 | XPC M90S UPS bundle; 6KVA/6KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC4 4 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) Power Module, (1) Battery Module providing 9 minutes runtime @ 6KVA/6KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 33"H. Weight: 275 lbs. | 11211
| M90S-4S6K2 | XPC M90S UPS bundle; 6KVA/6KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC4 4 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) Power Module, (2) Battery Modules providing 22 minutes runtime @ 6KVA/6KW load, RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 33"H. Weight: 382 lbs. | 13243
| M90S-4S6K3 | XPC M90S UPS bundle; 6KVA/6KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC4 4 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) Power Module, (3) Battery Modules providing 35 minutes runtime @ 6KVA/6KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 33"H. Weight: 489 lbs. | 15275
M90S 4-Slot 12KVA Hardwired Bundled Solutions
Part Number | Model | Description | List Price
| M90S-4S12K2 | XPC M90S UPS bundle; 12KVA/12KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC4 4 Slot Enclosure with Integral Front Access Maintenance Bypass, (2) Power Modules, (2) Battery Modules providing 9 minutes runtime @ 12KVA/12KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 33"H. Weight: 420 lbs. | 17370
M90S 6-Slot 6KVA Hardwired Bundled Solutions
Part Number | Model | Description | List Price
| M90S-6S6K1 | XPC M90S UPS bundle; 6KVA/6KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) Power Module, (1) Battery Module providing 9 minutes runtime @ 6KVA/6KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 314 lbs. | 13787
| M90S-6S6K2 | XPC M90S UPS bundle; 6KVA/6KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) Power Module, (2) Battery Modules providing 22 minutes runtime @ 6KVA/6KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 421 lbs. | 15819
| M90S-6S6K3 | XPC M90S UPS bundle; 6KVA/6KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) Power Module, (3) Battery Modules providing 35 minutes runtime @ 6KVA/6KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 528 lbs. | 17851
| M90S-6S6K4 | XPC M90S UPS bundle; 6KVA/6KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) Power Module, (4) Battery Modules providing 50 minutes runtime @ 6KVA/6KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 635 lbs. | 19883
| M90S-6S6K5 | XPC M90S UPS bundle; 6KVA/6KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) Power Module, (5) Battery Modules providing 66 minutes runtime @ 6KVA/6KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 742 lbs. | 21915
M90S 6-Slot 12KVA Hardwired Bundled Solutions
Part Number | Model | Description | List Price
| M90S-6S12K2 | XPC M90S UPS bundle; 12KVA/12KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (2) Power Modules, (2) Battery Modules providing 9 minutes runtime @ 12KVA/12KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 459 lbs. | 19946
| M90S-6S12K3 | XPC M90S UPS bundle; 12KVA/12KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (2) Power Modules, (3) Battery Modules providing 15 minutes runtime @ 12KVA/12KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 566 lbs. | 21978
| M90S-6S12K4 | XPC M90S UPS bundle; 12KVA/12KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (2) Power Modules, (4) Battery Modules providing 22 minutes runtime @ 12KVA/12KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); , Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 673 lbs. | 24010
M90S 6-Slot 18KVA Hardwired Bundled Solutions
Part Number | Model | Description | List Price
| M90S-6S18K3 | XPC M90S UPS bundle; 18KVA/18KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (3) Power Modules, (3) Battery Modules providing 9 minutes runtime @ 18KVA/18KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 604 lbs. | 26105
M90S 6-Slot 24KVA Hardwired Bundled Solutions
Part Number | Model | Description | List Price
| M90S-6S24K4 | XPC M90S / BC7 UPS bundle; 24KVA/24KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (4) Power Modules, (2) Battery Modules,and M90S-BC7-2 Bundle providing 9 minutes runtime @ 24KVA/24KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. UPS Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 535 lbs BC7 Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 376 lbs | 39798
M90S Battery Cabinet Bundles
Part Number | Model | Description | List Price
| M90S-BC7-1 | XPC M90S Battery Cabinet bundle; Includes XPC M90S-BC7 7 Slot External Battery Enclosure; (1) battery module; DC Breaker; Casters. 3 year battery warranty (USA and Canada). Increases runtime to __ minutes runtime @ __KVA/__KW load; Enclosure and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 269 lbs | 7408
| M90S-BC7-2 | XPC M90S Battery Cabinet bundle; Includes XPC M90S-BC7 7 Slot External Battery Enclosure; (2) battery modules; DC Breaker; Casters. 3 year battery warranty (USA and Canada). Increases runtime to __ minutes runtime @ __KVA/__KW load; Enclosure and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 376 lbs | 9440
| M90S-BC7-3 | XPC M90S Battery Cabinet bundle; Includes XPC M90S-BC7 7 Slot External Battery Enclosure; (3) battery modules; DC Breaker; Casters. 3 year battery warranty (USA and Canada). Increases runtime to __ minutes runtime @ __KVA/__KW load; Enclosure and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 483 lbs | 11472
| M90S-BC7-4 | XPC M90S Battery Cabinet bundle; Includes XPC M90S-BC7 7 Slot External Battery Enclosure; (4) battery modules; DC Breaker; Casters. 3 year battery warranty (USA and Canada). Increases runtime to __ minutes runtime @ __KVA/__KW load; Enclosure and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 590 lbs | 13504
| M90S-BC7-5 | XPC M90S Battery Cabinet bundle; Includes XPC M90S-BC7 7 Slot External Battery Enclosure; (5) battery modules; DC Breaker; Casters. 3 year battery warranty (USA and Canada). Increases runtime to __ minutes runtime @ __KVA/__KW load; Enclosure and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 697 lbs | 15536
| M90S-BC7-6 | XPC M90S Battery Cabinet bundle; Includes XPC M90S-BC7 7 Slot External Battery Enclosure; (6) battery modules; DC Breaker; Casters. 3 year battery warranty (USA and Canada). Increases runtime to __ minutes runtime @ __KVA/__KW load; Enclosure and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 804 lbs | 17568
| M90S-BC7-7 | XPC M90S Battery Cabinet bundle; Includes XPC M90S-BC7 7 Slot External Battery Enclosure; (7) battery modules; DC Breaker; Casters. 3 year battery warranty (USA and Canada). Increases runtime to __ minutes runtime @ __KVA/__KW load; Enclosure and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 911 lbs | 19600
M90S External Bypass Options
| 90885-C241310ECA050A05013MB | Three-Breaker Maintenance Bypass Switch; 240VAC, Single-Phase, 50 A, 10kAIC; rated for up to 8KVA; Wallmount; includes UPS Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker,interlock plate, lockable front panel, UL981, Black. 22"W x 24"H x 9"D; 55 lbs. | Call for Price
| 90885-C241310ECA070A07013MB | Three-Breaker Maintenance Bypass Switch; 240VAC, Single-Phase, 70 A, 10kAIC; rated for up to 12KVA; Wallmount; includes UPS Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker,interlock plate, lockable front panel, UL981, Black. 22"W x 24"H x 9"D; 55 lbs. | Call for Price
| 90885-C241310ECA125A12513MB | Three-Breaker Maintenance Bypass Switch; 240VAC, Single-Phase, 125 A, 10kAIC; rated for up to 20KVA; Wallmount; includes UPS Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel, UL981, Black. 22"W x 24"H x 9"D; 55 lbs. | Call for Price
| 90885-C241310ECA150A15013MB | Three-Breaker Maintenance Bypass Switch; 240VAC, Single-Phase, 150 A, 10kAIC; rated for up to 25KVA; Wallmount; includes UPS Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel, UL981, Black. 22"W x 24"H x 9"D; 55 lbs. | Call for Price
M90S Output Cords
Part Number | Model | Description | List Price
| XPC-ZLC20-620R | Optional 12" output cord, Locking C20 to 6-20 receptacle for use with M90S; 3 lbs. | 79
| XPC-ZLC20-L620R | Optional 12" output cord, Locking C20 to L6-20 receptacle for use with M90S; 3 lbs. | 79
| XPC-ZLC20-L630R | Optional 12" output cord, Locking C20 to L6-30 receptacle for use with M90S; L6-30R protected by 20A breaker; 3 lbs. | 79
| XPC-C20-L615R | Optional 12" output cord, C20 to L6-15 receptacle for use with M90S; 3 lbs. | 45
Connectivity Options
Part Number | Model | Description | List Price
90000698 | SNMP-M90S | Internal SNMP/WEB Card for use with M90S Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Packaging = 7.25"W x 6.0"D x 2.5"H, 1.0 lbs | 339
90000398 | SNMP-EMD | Environmental Monitoring Sensor to monitor room temperature and humidity - used with SNMP-M90S SNMP/WEB Card. Packaging = 7.25"W x 6.0"D x 2.5"H, 1.0 lbs | 180
90000267 | MODBUS-IN | MODBUS CARD for use with theM90S Series UPS; packaging = 7.25" x 6.0" x 2.5", 1.0 lbs | 319
90000265 | RELAY-MINI | Dry Contact RELAY CARD with DB9 & terminal block adapter; packaging = 7.25" x 6.0" x 2.5", 1.0 lbs | 120
Warranty and Service Options
Part Number | Model | Description | List Price
90001282 | 9SUS8051 | M90S 5x8 Startup and 1 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 3900
90001283 | 9SUS8052 | M90S 5x8 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 4500
90001284 | 9USUS8053 | M90S 5x8 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5100
90001285 | 9SU724051 | M90S 7x24 Startup and 1 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5070
90001286 | 9SU724052 | M90S 7x24 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5850
90001287 | 9SU724053 | M90S 7x24 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioningof UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 6630
90001288 | 9PM58 | M90S Preventative Maintenance Service, 5x8. For Zone 1 (within 100 miles of XPC Service Center). | 3500
90001289 | 9PM724 | M90S Preventative Maintenance Service, 7x24. For Zone 1 (within 100 miles of XPC Service Center). | 4550
90000538 | SVCADD | Service adder for locations further than 100 miles. | 1050
M90S-12S Series Modular Double Conversion Split-Phase
M90S Series Ala Carte Solutions
Part Number | Model | Description | List Price
90001272 | M90S-ENC12 | XPC M90S 12-slot enclosure; Up to 48kVA/48kW; On Line - Tower configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" color touch screen, Casters, Integral Front Access Three-Breaker Maintenance Bypass switch, Floor mount bracket; Communications Module; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus) Communication Software and Cable; UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Power Modules and Battery Modules purchased separately; Dims: 23.6"W X 36"D x 79.1"H. Weight: 480 lbs. | 28400
90000693 | M90S-PWM6 | 6KVA/6KW Power Module for XPC M90S UPS; On Line- 120/208V In-120/208V Out or 120/240V In - 120/240V Out; LCD Screen, Dims: 16.3"W X 24"D x 5.2"H (3U). Weight: 38 lbs. | 4190
90001262 | M90S-BMXRV2 | Battery Module for XPC M90S UPS; Contains two battery sleeves, each containing (8) 12V 580W batteries; battery breaker; 16.3"W X 24"D x 5.2"H. Weight: 107 lbs. Note: Minimum of one battery module required for each power module used for capacity. | 2095
90000716 | M90-BC | M90S-12S Matching External Modular Battery Cabinet. Holds up to (32) x M90-BCBAT Battery Modules; 2 Year Warranty, Dims 23.6"W x 43.3"D x 79.1"H, Weight 416 lbs. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M90S-12S | 12200
90000764 | M90-BCBAT | Battery Module for M90-BC External Battery Cabinet. Contains (5) CSB HR1290 Batteries each, 4 battery modules required per string, must be purchased in multiplies of 4, (xx) battery modules will provide ___ minutes runtime @ ___kW load, Dims: 7.3"W x 38.5"D x 3.2"H, Weight 85 lbs. | 1025
90000678 | M90S12S-SEIS | Seismic Hold Down Achorage for M90S-ENC12 enclosure. Includes calculations with State of California Engineer Stamp. | 1900
90001213 | M90-CBL | Cable kit for connecting M90-BC battery cabinet to M90S-12S UPS. Includes 8’ cables and lugs. Pricing for longer length cables is available upon request. | 1050
M90S 12-Slot 18KVA Bundled Solutions
Part Number | Model | Description | List Price
Bundle | M90S-12S18K0 | XPC M90S UPS bundle; 18KVA/18KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (3) Power Modules; setup for external batteries; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure and Power Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 594 lbs. External batteries ordered seperately. | 40970
Bundle | M90S-12S18K3 | XPC M90S UPS bundle; 18KVA/18KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (3) Power Modules; (3) Battery Modules providing 9 minutes runtime @ 18KVA/18KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 915 lbs. | 47255
Bundle | M90S-12S18K4 | XPC M90S UPS bundle; 18KVA/18KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (3) Power Modules; (4) Battery Modules providing 14 minutes runtime @ 18KVA/18KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1022 lbs. | 49350
Bundle | M90S-12S18K5 | XPC M90S UPS bundle; 18KVA/18KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (3) Power Modules; (5) Battery Modules providing 18 minutes runtime @ 18KVA/18KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1129 lbs. | 51445
Bundle | M90S-12S18K6 | XPC M90S UPS bundle; 18KVA/18KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (3) Power Modules; (6) Battery Modules providing 23 minutes runtime @ 18KVA/18KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1236 lbs. | 53540
Bundle | M90S-12S18K7 | XPC M90S UPS bundle; 18KVA/18KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (3) Power Modules; (7) Battery Modules providing 27 minutes runtime @ 18KVA/18KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1343 lbs. | 55635
Bundle | M90S-12S18K8 | XPC M90S UPS bundle; 18KVA/18KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (3) Power Modules; (8) Battery Modules providing 32 minutes runtime @ 18KVA/18KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1450 lbs. | 57730
Bundle | M90S-12S18K9 | XPC M90S UPS bundle; 18KVA/18KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (3) Power Modules; (9) Battery Modules providing 37 minutes runtime @ 18KVA/18KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1557 lbs. | 59825
M90S 12-Slot 24KVA Bundled Solutions
Part Number | Model | Description | List Price
Bundle | M90S-12S24K0 | XPC M90S UPS bundle; 24KVA/24KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (4) Power Modules; setup for external batteries; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure and Power Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 632 lbs. External batteries ordered seperately. | 45160
Bundle | M90S-12S24K3 | XPC M90S UPS bundle; 24KVA/24KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (4) Power Modules; (3) Battery Modules providing 6 minutes runtime @ 24KVA/24KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 953 lbs. | 51445
Bundle | M90S-12S24K4 | XPC M90S UPS bundle; 24KVA/24KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (4) Power Modules; (4) Battery Modules providing 9 minutes runtime @ 24KVA/24KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1060 lbs. | 53540
Bundle | M90S-12S24K5 | XPC M90S UPS bundle; 24KVA/24KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (4) Power Modules; (5) Battery Modules providing 13 minutes runtime @ 24KVA/24KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1167 lbs. | 55635
Bundle | M90S-12S24K6 | XPC M90S UPS bundle; 24KVA/24KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (4) Power Modules; (6) Battery Modules providing 16 minutes runtime @ 24KVA/24KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1274 lbs. | 57730
Bundle | M90S-12S24K7 | XPC M90S UPS bundle; 24KVA/24KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (4) Power Modules; (7) Battery Modules providing 19 minutes runtime @ 24KVA/24KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1381 lbs. | 59825
Bundle | M90S-12S24K8 | XPC M90S UPS bundle; 24KVA/24KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (4) Power Modules; (8) Battery Modules providing 23 minutes runtime @ 24KVA/24KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1488 lbs. | 61920
M90S 12-Slot 30KVA Bundled Solutions
Part Number | Model | Description | List Price
Bundle | M90S-12S30K0 | XPC M90S UPS bundle; 30KVA/30KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (5) Power Modules; setup for external batteries; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure and Power Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 670 lbs. External batteries ordered seperately. | 49350
Bundle | M90S-12S30K4 | XPC M90S UPS bundle; 30KVA/30KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (5) Power Modules; (4) Battery Modules providing 7 minutes runtime @ 30KVA/30KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 991 lbs. | 57730
Bundle | M90S-12S30K5 | XPC M90S UPS bundle; 30KVA/30KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (5) Power Modules; (5) Battery Modules providing 9 minutes runtime @ 30KVA/30KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1098 lbs. | 59825
Bundle | M90S-12S30K6 | XPC M90S UPS bundle; 30KVA/30KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (5) Power Modules; (6) Battery Modules providing 12 minutes runtime @ 30KVA/30KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1205 lbs. | 61920
Bundle | M90S-12S30K7 | XPC M90S UPS bundle; 30KVA/30KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (5) Power Modules; (7) Battery Modules providing 15 minutes runtime @ 30KVA/30KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1312 lbs. | 64015
M90S 12-Slot 36KVA Bundled Solutions
Part Number | Model | Description | List Price
Bundle | M90S-12S36K0 | XPC M90S UPS bundle; 36KVA/36KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (6) Power Modules; setup for external batteries; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure and Power Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 708 lbs. External batteries ordered seperately. | 53540
Bundle | M90S-12S36K5 | XPC M90S UPS bundle; 36KVA/36KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (6) Power Modules; (5) Battery Modules providing 7 minutes runtime @ 36KVA/36KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1243 lbs. | 64015
Bundle | M90S-12S36K6 | XPC M90S UPS bundle; 36KVA/36KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (6) Power Modules; (6) Battery Modules providing 9 minutes runtime @ 36KVA/36KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1350 lbs. | 66110
M90S 12-Slot 42KVA Bundled Solutions
Part Number | Model | Description | List Price
Bundle | M90S-12S42K0 | XPC M90S UPS bundle; 42KVA/42KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (7) Power Modules; setup for external batteries; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure and Power Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 746 lbs. External batteries ordered seperately. | 57730
Bundle | M90S-12S42K5 | XPC M90S UPS bundle; 42KVA/42KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (7) Power Modules; (5) Battery Modules providing 6 minutes runtime @ 42KVA/42KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1281 lbs. | 68205
M90S 12-Slot 48KVA Bundled Solutions
Part Number | Model | Description | List Price
Bundle | M90S-12S48K0 | XPC M90S UPS bundle; 48KVA/48KW; On Line-Tower Configuration, 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (8) Power Modules; setup for external batteries; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure and Power Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 746 lbs. External batteries ordered seperately. | 61920
M90-BC Modular Battery Cabinet Bundles
Part Number | Model | Description | List Price
Bundle | M90-BC-04B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (4) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 756 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M90S-12S Cable Available. | 16300
Bundle | M90-BC-08B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (8) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 1096 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M90S-12S Cable Available. | 20400
Bundle | M90-BC-12B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (12) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 1436 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M90S-12S Cable Available. | 24500
Bundle | M90-BC-16B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (16) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 1776 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M90S-12S Cable Available. | 28600
Bundle | M90-BC-20B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (20) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 2116 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M90S-12S Cable Available. | 32700
Bundle | M90-BC-24B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (24) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 2456 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M90S-12S Cable Available. | 36800
Bundle | M90-BC-28B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (28) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 2796 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M90S-12S Cable Available. | 40900
Bundle | M90-BC-32B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (32) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Each battery string (4 modules) protected by a 100A breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 3136 lbs. Battery modules shipped on separate pallet. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M90S-12S Cable Available. | 45000
Connectivity Options
Part Number | Model | Description | List Price
90000698 | SNMP-M90S | Internal SNMP/WEB Card for use with M90S Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Packaging = 7.25"W x 6.0"D x 2.5"H, 1.0 lbs | 339
90000398 | SNMP-EMD | Environmental Monitoring Sensor to monitor room temperature and humidity - used with SNMP-M90S SNMP/WEB Card. Packaging = 7.25"W x 6.0"D x 2.5"H, 1.0 lbs | 180
90000267 | MODBUS-IN | MODBUS CARD for use with the P90L Series UPS; packaging = 7.25" x 6.0" x 2.5", 1.0 lbs | 319
Warranty and Service Options
Part Number | Model | Description | List Price
90001282 | M90S12SSU583 | Upgrade standard warranty to 5x8 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance and (1) PM (5X8) to be perfromed at beginning of year three. | 6500
90001249 | M90S12SSU72 | Upgrade Standard 5x8 Warranty to 7x24 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 2800
90001284 | M90S12SSU73 | Upgrade Standard Warranty to 7x24 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioningof UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance and (1) PM (7x24) to be perfromed at beginning of year three. | 9300
90001285 | M90S12S1YREE | M90S-12S One Year extension of factory on-site warranty, electronics only. Covers parts and labor, extending the standard warranty by 1 year. Includes (1) PM (7x24) to be perfromed at beginning of the extension year. For Zone 1 (within 100 miles of XPC Service Center). | 8800
90001286 | M90S12SSPM7 | M90S-12S Preventative Maintenance Service, 7x24. For Zone 1 (within 100 miles of XPC Service Center). | 5850
90000538 | SVCADD | Service adder for locations further than 100 miles. | 1200
Li90 Series Double Conversion 3-Phase (with Lithium Batteries)
Part Number | Model | Description | List Price
Bundle | Li90-10k1 | Xtreme Power Li90 Series online 10KVA/10KW, 208/120 VAC three-phase UPS with one internal lithium battery module for 15 minutes full load runtime. Includes color touch screen display, static switch, and maintenance bypass switch ; up to 40A charge current, 94.5% efficiency in online mode or 99% efficiency in ECO mode; standard local EPO, RS485 ports; (5) output dry contacts; (2) input dry contacts; (1) card slot for Web/SNMP; UL-1778 (TUV), UL 38.3, UL1973 ; 2 Year On-site UPS Warranty (USA and Canada); 5 Year Battery Warranty; 5x8 Start-up included. Can accommodate up to three battery modules for extended runtimes; 12.6" W x 35.2" D x 49.2" H. 287 lbs. | 29500
Bundle | Li90-10k2 | Xtreme Power Li90 Series online 10KVA/10KW, 208/120 VAC three-phase UPS with two internal lithium battery modules for 30 minutes full load runtime. Includes color touch screen display, static switch, and maintenance bypass switch ; up to 40A charge current, 94.5% efficiency in online mode or 99% efficiency in ECO mode; standard local EPO, RS485 ports; (5) output dry contacts; (2) input dry contacts; (1) card slot for Web/SNMP; UL-1778 (TUV), UL 38.3, UL1973 ; 2 Year On-site UPS Warranty (USA and Canada); 5 Year Battery Warranty; 5x8 Start-up included. Can accommodate up to three battery modules for extended runtimes; 12.6" W x 35.2" D x 49.2" H. 367 lbs. | 38000
Bundle | Li90-10k3 | Xtreme Power Li90 Series online 10KVA/10KW, 208/120 VAC three-phase UPS with three internal lithium battery modules for 45 minutes full load runtime. Includes color touch screen display, static switch, and maintenance bypass switch ; up to 40A charge current, 94.5% efficiency in online mode or 99% efficiency in ECO mode; standard local EPO, RS485 ports; (5) output dry contacts; (2) input dry contacts; (1) card slot for Web/SNMP; UL-1778 (TUV), UL 38.3, UL1973 ; 2 Year On-site UPS Warranty (USA and Canada); 5 Year Battery Warranty; 5x8 Start-up included. 12.6" W x 35.2" D x 49.2" H. 447 lbs. | 46500
Bundle | Li90-20k2 | Xtreme Power Li90 Series online 20KVA/20KW, 208/120 VAC three-phase UPS with two internal lithium battery modules for 15 minutes full load runtime. Includes color touch screen display, static switch, and maintenance bypass switch ; up to 40A charge current, 94.5% efficiency in online mode or 99% efficiency in ECO mode; standard local EPO, RS485 ports; (5) output dry contacts; (2) input dry contacts; (1) card slot for Web/SNMP; UL-1778 (TUV), UL 38.3, UL1973 ; 2 Year On-site UPS Warranty (USA and Canada); 5 Year Battery Warranty; 5x8 Start-up included. Can accommodate up to three battery modules for extended runtimes; 12.6" W x 35.2" D x 49.2" H. 387 lbs. | 45000
Bundle | Li90-20k3 | Xtreme Power Li90 Series online 20KVA/20KW, 208/120 VAC three-phase UPS with three internal lithium battery module for 22 minutes full load runtime. Includes color touch screen display, static switch, and maintenance bypass switch ; up to 40A charge current, 94.5% efficiency in online mode or 99% efficiency in ECO mode; standard local EPO, RS485 ports; (5) output dry contacts; (2) input dry contacts; (1) card slot for Web/SNMP; UL-1778 (TUV), UL 38.3, UL1973 ; 2 Year On-site UPS Warranty (USA and Canada); 5 Year Battery Warranty; 5x8 Start-up included. 12.6" W x 35.2" D x 49.2" H. 467 lbs. | 53500
Bundle | Li90-30k3 | Xtreme Power Li90 Series online 30KVA/30KW, 208/120 VAC three-phase UPS with three internal lithium battery module for 15 minutes full load runtime. Includes color touch screen display, static switch, and maintenance bypass switch ; up to 40A charge current, 94.5% efficiency in online mode or 99% efficiency in ECO mode; standard local EPO, RS485 ports; (5) output dry contacts; (2) input dry contacts; (1) card slot for Web/SNMP; UL-1778 (TUV), UL 38.3, UL1973 ; 2 Year On-site UPS Warranty (USA and Canada); 5 Year Battery Warranty; 5x8 Start-up included. 12.6" W x 35.2" D x 49.2" H. 483 lbs. | 59000
Connectivity Options
Part Number | Model | Description | List Price
90001245 | SNMP-2PG1 | Internal two port SNMP/WEB Card for use with X90, M90C, M90, M90L E91, and M90S Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-TMPH temperature and humidity probe; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 715
90000398 | SNMP-TMPH | Temperature and humidity Probe - used with SNMP-2PG1 SNMP/WEB Card. Packaging = 7.25"W x 6.0"D x 2.5"H, 1.0 lbs | 329
Service Options
Part Number | Model | Description | List Price
90001348 | Li901U58 | Li90 UPS Warranty Upgrade from 2-Year 5x8 On-Site to 3-Year 5x8 On-Site. Includes (1) 5x8 PM to be beformed at the beginning of year three. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5500
90001349 | Li902U58 | Li90 UPS Warranty Upgrade from 2-Year 5x8 On-Site to 5-Year 5x8 On-Site. Includes (2) 5x8 PMs to be beformed at the beginning of year three and beginning of year 5. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 13500
90001350 | Li90724 | Li90 UPS Warranty Upgrade from 2-Year 5x8 On-Site to 2-Year 7x24 On-Site. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 2800
90001351 | li901U724 | Li90 UPS Warranty Upgrade from 2-Year 5x8 On-Site to 3-Year 7x24 On-Site. Includes (1) 7x24 PM to be beformed at the beginning of year three. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 8000
90001352 | Li90PM24 | Li90 Preventative Maintenance Service, 7x24. For Zone 1 (within 100 miles of XPC Service Center). | 5800
90000538 | SVCADD | Service adder for locations further than 100 miles. | 1050
E91 Series Double Conversion 3-Phase (with Internal Batteries)
Part Number | Model | Description | List Price
90000975 | E91-10K | Xtreme Power E91 Series online 10KVA/10KW, 208/120 VAC three-phase UPS with 2 strings of internal batteries for 11 minutes full load runtime. Includes color touch screen display, static switch, and maintenance bypass switch ; up to 12A charge current, 94% efficiency in online mode or 98% efficiency in ECO mode; standard RS232, EPO, RS485, and USB communication ports; (1) card slot for Web/SNMP or Relay cards; UL-1778 (TUV), cUL, FCCA, Energy Star 2.0 ; 2 Year Standard Warranty (USA and Canada); Start-up and onsite labor is not included; Can accommodate external battery packs for extended runtimes; 9.9" W x 26.3" D x 32.3" H. 273 lbs. | 10800
90000976 | E91-15K | Xtreme Power E91 Series online 15KVA/15KW, 208/120 VAC three-phase UPS with 3 strings of internal batteries for 11 minutes full load runtime. Includes color touch screen display, static switch, and maintenance bypass switch ; up to 12A charge current, 94% efficiency in online mode or 98% efficiency in ECO mode; standard RS232, EPO, RS485, and USB communication ports; (1) card slot for Web/SNMP or Relay cards; UL-1778 (TUV), cUL, FCCA, Energy Star 2.0 ; 2 Year Standard Warranty (Usa and Canada); Start-up and onsite labor is not included; Can accommodate external battery packs for extended runtimes; 11.9" W x 34" D x 40.2" H. 306 lbs. | 12700
90000977 | E91-20K | Xtreme Power E91 Series online 20KVA/20KW, 208/120 VAC three-phase UPS with 3 strings of internal batteries for 7 minutes full load runtime. Includes color touch screen display, static switch, and maintenance bypass switch ; up to 12A charge current, 94% efficiency in online mode or 98% efficiency in ECO mode; standard RS232, EPO, RS485, and USB communication ports; (1) card slot for Web/SNMP or Relay cards; UL-1778 (TUV), cUL, FCCA, Energy Star 2.0 ; 2 Year Standard Warranty (USA and Canada); Start-up and onsite labor is not included; Can accommodate external battery packs for extended runtimes; 11.9" W x 34" D x 40.2" H. 306 lbs. | 13600
90000980 | E91-20KL | Xtreme Power E91 Series online 20KVA/20KW, 208/120 VAC three-phase UPS with no internal batteries. Includes color touch screen display, static switch, and maintenance bypass switch ; up to 12A charge current, 94% efficiency in online mode or 98% efficiency in ECO mode; standard RS232, EPO, RS485, and USB communication ports; (1) card slot for Web/SNMP or Relay cards; UL-1778 (TUV), cUL, FCCA, Energy Star 2.0 ; 2 Year Standard Warranty (USA and Canada); Start-up and onsite labor is not included; 11.9" W x 34" D x 40.2" H. 296 lbs. External battery packs must be ordered seperately. | 11800
90000979 | E91-30K | Xtreme Power E91 Series online 30KVA/30KW, 208/120 VAC three-phase UPS with 3 strings of internal batteries for 6 minutes full load runtime. Includes color touch screen display, static switch, and maintenance bypass switch; Front access only design; up to 16A charge current, 94% efficiency in online mode or 98% efficiency in ECO mode; standard RS232, EPO, RS485, and USB communication ports; (1) card slot for Web/SNMP or Relay cards; UL-1778 (TUV), cUL, FCC; 2 Year Standard Warranty (USA and Canada); Start-up and onsite labor is not included; Can accommodate external battery packs for extended runtimes; 23.6" W x 36.3" D x 65.6" H. 496 lbs. | 21800
90001234 | E91-30K4 | Xtreme Power E91 Series online 30KVA/30KW, 208/120 VAC three-phase UPS with 4 strings of internal batteries for 9 minutes full load runtime. Includes color touch screen display, static switch, and maintenance bypass switch; Front access only design; up to 16A charge current, 94% efficiency in online mode or 98% efficiency in ECO mode; standard RS232, EPO, RS485, and USB communication ports; (1) card slot for Web/SNMP or Relay cards; UL-1778 (TUV), cUL, FCC; 2 Year Standard Warranty (USA and Canada); Start-up and onsite labor is not included; Can accommodate external battery packs for extended runtimes; 23.6" W x 36.3" D x 65.6" H. 549 lbs. | 23700
90000981 | E91-30KL | Xtreme Power E91 Series online 30KVA/30KW, 208/120 VAC three-phase UPS no internal batteries. Includes color touch screen display, static switch, and maintenance bypass switch; Front access only design; up to 16A charge current, 94% efficiency in online mode or 98% efficiency in ECO mode; standard RS232, EPO, RS485, and USB communication ports; (1) card slot for Web/SNMP or Relay cards; UL-1778 (TUV), cUL, FCC; 2 Year Standard Warranty (USA and Canada); Start-up and onsite labor is not included; 23.6" W x 36.3" D x 65.6" H. 419 lbs. External battery packs must be ordered seperately. | 17000
90000980 | E91-40K | Xtreme Power E91 Series online 40KVA/40KW, 208/120 VAC three-phase UPS with 4 strings of internal batteries for 6 minutes full load runtime. Includes color touch screen display, static switch, and maintenance bypass switch; Front access only design; up to 16A charge current, 94% efficiency in online mode or 98% efficiency in ECO mode; standard RS232, EPO, RS485, and USB communication ports; (1) card slot for Web/SNMP or Relay cards; UL-1778 (TUV), cUL, FCC; 2 Year Standard Warranty (USA and Canada); Start-up and onsite labor is not included; Can accommodate external battery packs for extended runtimes; 23.6" W x 36.3" D x 65.6" H. 551 lbs. | 25300
90000982 | E91-40KL | Xtreme Power E91 Series online 40KVA/40KW, 208/120 VAC three-phase UPS with no internal batteries. Includes color touch screen display, static switch, and maintenance bypass switch; Front access only design; up to 16A charge current, 94% efficiency in online mode or 98% efficiency in ECO mode; standard RS232, EPO, RS485, and USB communication ports; (1) card slot for Web/SNMP or Relay cards; UL-1778 (TUV), cUL, FCC; 2 Year Standard Warranty (USA and Canada); Start-up and onsite labor is not included; 23.6" W x 36.3" D x 65.6" H. 539 lbs. External battery packs must be ordered seperately. | 18500
External Battery for use with E91 UPS (With Batteries)
Part Number | Model | Description | List Price
90000984 | EBP09-2 | Line and Match External Battery Pack for E91 10KVA, 15kVA, and 20kVA UPS. Includes (40) 12V 9AH batteries; Up to four battery packs per UPS can be used for extended runtime applications; (_) battery packs provides (__) minutes of runtime @ __KW load. 11.9"W x 34"D x 40.2"H. 310 lbs. | 6100
90000985 | EBP09-5 | Line and Match External Battery Pack for E91 10KVA, 15kVA, and 20kVA UPS. Includes (100) 12V 9AH batteries; Up to four battery packs per UPS can be used for extended runtime applications; (_) battery packs provides (__) minutes of runtime @ __KW load. 11.9"W x 34"D x 40.2"H. 670 lbs. | 9950
90000986 | EBP10-5 | Line and Match External Battery Pack for E91 30KVA/30KW or 40KVA/40KW UPS. Includes (100) 12V 580W batteries; Up to four battery packs per UPS can be used for extended runtime applications; (_) battery packs provides (__) minutes of runtime @ __KW load. 11.9"W x 34"D x 40.2"H. 770 lbs. | 11700
PDU Options (Rear mounted)
Part Number | Model | Description | List Price
90001023 | E91-PDU1 | E91 rear mounted PDU. Configured with (4) L21-20R outlets each protected by a 20A breaker. 9.5"W x 4.3"D x 11.6"H; 15 lbs *Optional Power Distributions Units may not be used with external maintenance bypass. | 1350
90001024 | E91-PDU2 | E91 rear mounted PDU. Configured with (4) L21-30R outlets each protected by a 30A breaker. 9.5"W x 4.3"D x 11.6"H; 15 lbs *Optional Power Distributions Units may not be used with external maintenance bypass. | 1500
External Maintenance Bypass Options (wallmount)
Part Number | Model | Description | List Price
| 90885-C208310ECA040A04013MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 40 A, 10kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 22"W x 24"H x 9"D; 55 lbs. For use with E91 10kVA UPS | Call For Price
| 90885-C208310ECA060A06013MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 60 A, 10kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 22"W x 24"H x 9"D; 55 lbs. For Use with E91 and all M90 Family 15kVA UPS | Call For Price
| 90885-C208310ECA080A08013MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 80 A, 10kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 22"W x 24"H x 9"D; 55 lbs. For Use with E91 and all M90 Family 20kVA UPS | Call For Price
| 90880-C208322ECA125A12502MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 125 A, 22kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 30"W x 36"H x 10"D; 110 lbs. For Use with E91 and all M90 Family 30kVA UPS | Call For Price
| 90880-C208322ECA150A15002MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 150 A, 22kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 30"W x 36"H x 10"D; 110 lbs. For Use with E91 40kVA UPS | Call For Price
Note: | E91 does not have Contacts to support SKRU.
Connectivity Options
Part Number | Model | Description | List Price
90001245 | SNMP-2PG1 | Internal two port SNMP/WEB Card for use with X90, M90C, M90, M90L E91, and M90S Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-TMPH temperature and humidity probe; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 715
90000267 | MODBUS-IN | MODBUS CARD for use with the E91, M90(U) and X90 Series UPS; packaging = 7.25" x 6" x 2.5", 1 lbs | 319
90000398 | SNMP-TMPH | Temperature and humidity Probe - used with SNMP-2PG1 SNMP/WEB Card. Packaging = 7.25"W x 6.0"D x 2.5"H, 1.0 lbs | 329
90000265 | RELAY-MINI | Dry Contact RELAY CARD with DB9 & terminal block adapter; packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 120
Service Options
Part Number | Model | Description | List Price
90001011 | E91SUS81 | E91 5x8 Startup and 1 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 3900
90001005 | E91SUS82 | E91 5x8 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 4500
90001006 | E91SUS83 | E91 5x8 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 7400
90001012 | E91SU7241 | E91 7x24 Startup and 1 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5070
90001007 | E91SU7242 | E91 7x24 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5850
90001235 | E91SU7243 | E91 7x24 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioningof UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 9620
90001236 | E91PM58 | E91 Preventative Maintenance Service, 5x8. For Zone 1 (within 100 miles of XPC Service Center). | 3500
90001010 | E91PM724 | E91 Preventative Maintenance Service, 7x24. For Zone 1 (within 100 miles of XPC Service Center). | 4550
90000538 | SVCADD | Service adder for locations further than 100 miles. | 1050
M90C Series Modular Double Conversion Three-Phase
M90C Series Ala Carte Solutions
Part Number | Model | Description | List Price
90001032 | M90C-ENC2 | XPC M90C 2-slot enclosure; 5kVA/5kW or 8kVA/8kW; On Line - Rack Mount or tower configuration, 120/208V Three-Phase In/Out , Hardwired in/out, Integral Rear Mounted Maintenance Bypass switch, RS-232, USB, EPO, intelligent slot for optional card (Web/SNMP, Relay, Modbus); Communication Software and Cable; UL-1778 (TUV), cUL, FCC, RoHS, TAA Compliant; 2 year UPS and battery warranty (USA and Canada). Power Module and Battery Module purchased separately; Unit Dims: 17.3"W X 31.5"D x 10.5"H. Weight: 38 lbs. | 2300
90001218 | M90C-ENC6 | XPC M90C 6-slot enclosure; Up to 24kVA/24kW; On Line - Tower configuration, 120/208V Three-Phase In/Out , Hardwired in/out, Large LCD Screen, Casters, Integral Front Access Maintenance Bypass switch, Floor mount bracket; Communications Module; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus) Communication Software and Cable; UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Power Modules, Battery Modules, and Blank Panels purchased separately; Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 169 lbs. | 8000
90001211 | M90C-PWM5 | 5KVA/5KW Power Module for XPC M90C UPS; On Line- 120/208V Three-Phase In- Out; LCD Screen, Dims: 16.3"W X 24"D x 5.2"H (3U). Weight: 38 lbs. | 4900
90001029 | M90C-PWM8 | 8KVA/8KW Power Module for XPC M90C UPS; On Line- 120/208V Three-Phase In- Out; LCD Screen, Dims: 16.3"W X 24"D x 5.2"H (3U). Weight: 38 lbs. | 5700
90001262 | M90S-BMXRV2 | Battery Module for XPC M90S UPS; Contains two battery sleeves, each containing (8) 12V 580W batteries; battery breaker; 16.3"W X 24"D x 5.2"H. Weight: 107 lbs. Note: Minimum of one battery module required for each power module used for capacity. | 2095
90000696 | M90S-BC7 | XPC M90S External Battery Enclosure; 7-slot enclosure holds up to (7) M90S-BMXR battery modules; Includes Casters. Battery Modules and Blank Panels purchased separately; Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 162 lbs. | 4935
90000719 | M90S-CB | Caster Base for M90C-ENC2 or M90S-ENC2. Locking casters. Dims: 17"W X 24"D x 4.0"H. Weight: 15 lbs. | 610
90000703 | M90S-BP | M90C or M90S Matching Blank Panel covers front of unused slots. Dims: 16.5"W X 2"D x 5.2"H. Weight: 5 lbs. | 63
90000695 | M90S-RAIL2S | M90S Rail Kit for M90C-ENC2 or M90S-ENC2 2-slot enclosure. Dims: 20"W X 4"D x 2.5"H. Weight: 5 lbs. | 155
90001219 | XPC-L21-20P | Optional 8' Input cord, Terminal to L21-20P for use with M90C-5kW; 10 lbs. | 420
90001220 | XPC-L21-30P | Optional 8' Input cord, Terminal to L21-30P for use with M90C-8kW; 10 lbs. | 420
| M90C6S-SEIS | Seismic Hold Down Achorage for M90C-ENC6 enclosure. Includes calculations with State of California Engineer Stamp. | 1900
M90C Series Optional Receptacle Panels (6S = up to 4 RP), (2S = up to 1 RP)
Part Number | Model | Description | List Price
90000699 | M90S-RPA | XPC M90C Optional Receptacle Panel for M90C-6S. Contains (8) 5-20R receptacles. Mounts to rear of UPS Chassis. Weight: 5 lbs. | 295
90000700 | M90S-RPB | XPC M90C Optional Receptacle Panel for M90C-6S. Contains (2) C19 and (4) 5-20R receptacles. Mounts to rear of UPS Chassis. Weight: 5 lbs. | 295
90000701 | M90S-RPC | XPC M90C Optional Receptacle Panel for M90C-6S. Contains (1) L6-30R and (2) C19 receptacles. Mounts to rear of UPS Chassis. Weight: 5 lbs. | 295
90000703 | M90S-RPD | XPC M90C Optional Receptacle Panel for M90C-6S. Contains (1) L14-30R and (2) C19 receptacles. Mounts to rear of UPS Chassis. Weight: 5 lbs. | 295
Bundle | M90S-RPE | XPC M90C Optional Receptacle Panel for M90C-6S. Contains (2) L6-20R and (4) 5-20R receptacles. Mounts to rear of UPS Chassis. Weight: 5 lbs. | 453
Bundle | M90S-RPF | XPC M90C Optional Receptacle Panel for M90C-6S. Contains (1) L6-30R, (1) L6-20R and (4) 5-20R receptacles. Mounts to rear of UPS Chassis. L6-30R protected by 20A breaker; Weight: 5 lbs. | 453
Bundle | M90S-RPG | XPC M90C Optional Receptacle Panel for M90C-6S. Contains (1) L6-30R and (2) L6-20R receptacles. Mounts to rear of UPS Chassis. Weight: 5 lbs. | 453
Bundle | M90S-RPH | XPC M90C Optional Receptacle Panel for M90C-6S. Contains (3) L6-30R receptacles. Mounts to rear of UPS Chassis. (2) L6-30R protected by 20A breakers; Weight: 5 lbs. | 453
90001058 | M90C-RPI | XPC M90C Optional Receptacle Panel for M90C-2S or M90C-6S. Contains (1) L21-20R receptacle protected by a 20A breaker. Mounts to rear of UPS Chassis. Weight: 6 lbs. | 395
90001059 | M90C-RPJ | XPC M90C Optional Receptacle Panel for M90C-2S or M90C-6S. Contains (1) L21-30R receptacle protected by a 30A breaker. Mounts to rear of UPS Chassis. Weight: 6 lbs. | 395
90001060 | M90C-RPK | XPC M90C Optional Receptacle Panel for M90C-2S or M90C-6S. Contains (2) L21-20R receptacles. Mounts to rear of UPS Chassis. Weight: 6 lbs. | 395
90001061 | M90C-RPL | XPC M90C Optional Receptacle Panel for M90C-2S or M90C-6S. Contains (2) L21-30R receptacles. Mounts to rear of UPS Chassis. Weight: 6 lbs. | 395
M90C-2S Series Hardwired Bundled Solutions
Part Number | Model | Description | List Price
Bundle | M90C-2S5K | XPC M90C UPS bundle; 5kVA/5kW; On Line-Rackmount Configuration, 120/208V Three-Phase In/Out, Hardwired in/out. Bundle includes M90C-ENC2 2-Slot Enclosure with Integral Maintenance Bypass, Rackmount rails; (1) 5kVA/5kW Power Module and (1) Battery Module providing 12 minutes runtime @ 5KVA/5KW load; RS-232, USB, EPO, intelligent slot for optional card (Web/SNMP, Relay, Modbus; ) Communication Software and Cable; UL-1778 (TUV), cUL, FCC, RoHS, TAA Compliant; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 17.5"W X 33.7"D x 10.5"H. Weight: 185 lbs. | 9450
Bundle | M90C-2S5KT | XPC M90C UPS bundle; 5kVA/5kW; On-Line Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out. Bundle includes M90C-ENC2 2-Slot Enclosure with Integral Maintenance Bypass, Caster Base; (1) 5kVA/5kW Power Module and (1) Battery Module providing 12 minutes runtime @ 5KVA/5KW load; RS-232, USB, EPO, intelligent slot for optional card (Web/SNMP, Relay, Modbus; ) Communication Software and Cable; UL-1778 (TUV), cUL, FCC, RoHS, TAA Compliant; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 17.5"W X 33.7"D x 14.5"H. Weight: 198 lbs. | 9905
Bundle | M90C-2S8K | XPC M90C UPS bundle; 8kVA/8kW; On Line-Rackmount Configuration, 120/208V Three-Phase In/Out, Hardwired in/out. Bundle includes M90C-ENC2 2-Slot Enclosure with Integral Maintenance Bypass, Rackmount rails; (1) 8kVA/8kW Power Module and (1) Battery Module providing 6 minutes runtime @ 8KVA/8KW load; RS-232, USB, EPO, intelligent slot for optional card (Web/SNMP, Relay, Modbus; ) Communication Software and Cable; UL-1778 (TUV), cUL, FCC, RoHS, TAA Compliant; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 17.5"W X 33.5"D x 10.5"H. Weight: 185 lbs. | 10250
Bundle | M90C-2S8KT | XPC M90C UPS bundle; 8kVA/8kW; On-Line Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out. Bundle includes M90C-ENC2 2-Slot Enclosure with Integral Maintenance Bypass, Caster Base; (1) 8kVA/8kW Power Module and (1) Battery Module providing 12 minutes runtime @ 8KVA/8KW load; RS-232, USB, EPO, intelligent slot for optional card (Web/SNMP, Relay, Modbus; ) Communication Software and Cable; UL-1778 (TUV), cUL, FCC, RoHS, TAA Compliant; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 14.5"H. Weight: 198 lbs. | 10705
M90C 6-Slot 5KVA Hardwired Bundled Solutions
Part Number | Model | Description | List Price
| M90C-6S5K1 | XPC M90C UPS bundle; 5KVA/5KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) 5kVA Power Module, (1) Battery Module providing 12 minutes runtime @ 5KVA/5KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 314 lbs. | 15247
| M90C-6S5K2 | XPC M90C UPS bundle; 5KVA/5KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) 5K Power Module, (2) Battery Modules providing 28 minutes runtime @ 5KVA/5KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 421 lbs. | 17279
| M90C-6S5K3 | XPC M90C UPS bundle; 5KVA/5KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) 5K Power Module, (3) Battery Modules providing 46 minutes runtime @ 5KVA/5KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 528 lbs. | 19311
| M90C-6S5K4 | XPC M90C UPS bundle; 5KVA/5KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) 5K Power Module, (4) Battery Modules providing 66 minutes runtime @ 5KVA/5KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 635 lbs. | 21343
| M90C-6S5K5 | XPC M90C UPS bundle; 5KVA/5KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) 5K Power Module, (5) Battery Modules providing 86 minutes runtime @ 5KVA/5KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 742 lbs. | 23375
M90C 6-Slot 8KVA Hardwired Bundled Solutions
Part Number | Model | Description | List Price
| M90C-6S8K1 | XPC M90C UPS bundle; 8KVA/8KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) 8kVA Power Module, (1) Battery Module providing 6 minutes runtime @ 8KVA/8KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 314 lbs. | 16047
| M90C-6S8K2 | XPC M90C UPS bundle; 8KVA/8KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) 8kVA Power Module, (2) Battery Module providing 16 minutes runtime @ 8KVA/8KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 421 lbs. | 18079
| M90C-6S8K3 | XPC M90C UPS bundle; 8KVA/8KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) 8kVA Power Module, (3) Battery Module providing 26 minutes runtime @ 8KVA/8KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 528 lbs. | 20111
| M90C-6S8K4 | XPC M90C UPS bundle; 8KVA/8KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) 8kVA Power Module, (4) Battery Module providing 37 minutes runtime @ 8KVA/8KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 635 lbs. | 22143
| M90C-6S8K5 | XPC M90C UPS bundle; 8KVA/8KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) 8kVA Power Module, (5) Battery Module providing 49 minutes runtime @ 8KVA/8KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 742 lbs. | 24175
M9C 6-Slot 10KVA Hardwired Bundled Solutions
Part Number | Model | Description | List Price
| M90C-6S10K2 | XPC M90C UPS bundle; 10KVA/10KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (2) 5kVA Power Modules, (2) Battery Module providing 12 minutes runtime @ 10KVA/10KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 459 lbs. | 22116
| M90C-6S10K3 | XPC M90C UPS bundle; 10KVA/10KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (2) 5kVA Power Modules, (3) Battery Module providing 20 minutes runtime @ 10KVA/10KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 566 lbs. | 24148
| M90C-6S10K4 | XPC M90C UPS bundle; 10KVA/10KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (2) 5kVA Power Modules, (4) Battery Module providing 28 minutes runtime @ 10KVA/10KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 673 lbs. | 26180
M90C 6-Slot 15KVA Hardwired Bundled Solutions
Part Number | Model | Description | List Price
| M90C-6S15K2 | XPC M90C UPS bundle; 15KVA/15KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (3) 5kVA Power Module, (2) Battery Module providing 7 minutes runtime @ 15KVA/15KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 604 lbs. | 26953
| M90C-6S15K3 | XPC M90C UPS bundle; 15KVA/15KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (3) 5kVA Power Module, (3) Battery Module providing 12 minutes runtime @ 15KVA/15KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 711 lbs. | 28985
M90C 6-Slot 16KVA Hardwired Bundled Solutions
Part Number | Model | Description | List Price
| M90C-6S16K2 | XPC M90C UPS bundle; 16KVA/16KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (2) 8kVA Power Module, (2) Battery Module providing 6 minutes runtime @ 16KVA/16KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 459 lbs. | 23716
| M90C-6S16K3 | XPC M90C UPS bundle; 16KVA/16KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (2) 8kVA Power Module, (3) Battery Module providing 11 minutes runtime @ 16KVA/16KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 566 lbs. | 25748
| M90C-6S16K4 | XPC M90C UPS bundle; 16KVA/16KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (2) 8kVA Power Module, (4) Battery Module providing 16 minutes runtime @ 16KVA/16KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 673 lbs. | 27780
M9C 6-Slot 24KVA Hardwired Bundled Solutions
Part Number | Model | Description | List Price
| M90C-6S24K3 | XPC M90C UPS bundle; 24KVA/24KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (3) 8kVA Power Module, (3) Battery Module providing 6 minutes runtime @ 24KVA/24KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 711 lbs. | 31385
M90C Battery Cabinet Bundles
Part Number | Model | Description | List Price
| M90S-BC7-1 | XPC M90C Battery Cabinet bundle; Includes XPC M90S-BC7 7 Slot External Battery Enclosure; (1) battery module; (6) blank panels; DC Breaker; Casters. 2 year battery warranty (USA and Canada). Increases runtime to __ minutes runtime @ __KVA/__KW load; Enclosure and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 269 lbs | 7408
| M90S-BC7-2 | XPC M90C Battery Cabinet bundle; Includes XPC M90S-BC7 7 Slot External Battery Enclosure; (2) battery module; (5) blank panels; DC Breaker; Casters. 2 year battery warranty (USA and Canada). Increases runtime to __ minutes runtime @ __KVA/__KW load; Enclosure and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 376 lbs | 9440
| M90S-BC7-3 | XPC M90C Battery Cabinet bundle; Includes XPC M90S-BC7 7 Slot External Battery Enclosure; (3) battery module; (4) blank panels; DC Breaker; Casters. 2 year battery warranty (USA and Canada). Increases runtime to __ minutes runtime @ __KVA/__KW load; Enclosure and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 483 lbs | 11472
| M90S-BC7-4 | XPC M90C Battery Cabinet bundle; Includes XPC M90S-BC7 7 Slot External Battery Enclosure; (4) battery module; (3) blank panels; DC Breaker; Casters. 2 year battery warranty (USA and Canada).. Increases runtime to __ minutes runtime @ __KVA/__KW load; Enclosure and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 590 lbs | 13504
| M90S-BC7-5 | XPC M90C Battery Cabinet bundle; Includes XPC M90S-BC7 7 Slot External Battery Enclosure; (5) battery module; (2) blank panels; DC Breaker; Casters. 2 year battery warranty (USA and Canada). Increases runtime to __ minutes runtime @ __KVA/__KW load; Enclosure and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 697 lbs | 15536
| M90S-BC7-6 | XPC M90C Battery Cabinet bundle; Includes XPC M90S-BC7 7 Slot External Battery Enclosure; (6) battery module; (1) blank panel; DC Breaker; Casters. 2 year battery warranty (USA and Canada). Increases runtime to __ minutes runtime @ __KVA/__KW load; Enclosure and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 804 lbs | 17568
| M90S-BC7-7 | XPC M90C Battery Cabinet bundle; Includes XPC M90S-BC7 7 Slot External Battery Enclosure; (7) battery modules; DC Breaker; Casters. 2 year battery warranty (USA and Canada).. Increases runtime to __ minutes runtime @ __KVA/__KW load; Enclosure and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 911 lbs | 19600
Connectivity Options
Part Number | Model | Description | List Price
90001245 | SNMP-2PG1 | Internal two port SNMP/WEB Card for use with M90C, M90 and M90L Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-TMPH teperature and humidity probe; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 715
90000398 | SNMP-TMPH | Temperature and humidity Probe - used with SNMP-2PG1 SNMP/WEB Card. Packaging = 7.25"W x 6.0"D x 2.5"H, 1.0 lbs | 329
90000267 | MODBUS-IN | MODBUS CARD for use with the XPC UPS; packaging = 7.25" x 6.0" x 2.5", 1.0 lbs | 319
Warranty and Service Options
Part Number | Model | Description | List Price
90001290 | MCSU58OS1 | M90C 5x8 Startup and 1 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 3900
90001291 | MCSU58OS2 | M90C 5x8 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 4500
90001292 | MCSU58OS3 | M90C 5x8 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5100
90001293 | MCSU724OS1 | M90C 7x24 Startup and 1 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5070
90001294 | MCSU724OS2 | M90C 7x24 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5850
90001295 | MCSU724OS3 | M90C 7x24 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioningof UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 6630
90001296 | MCPM58 | M90C Preventative Maintenance Service, 5x8. For Zone 1 (within 100 miles of XPC Service Center). | 3500
90001297 | MCPM724 | M90C Preventative Maintenance Service, 7x24. For Zone 1 (within 100 miles of XPC Service Center). | 4550
90000538 | SVCADD | Service adder for locations further than 100 miles. | 1050
M90U and M90LU (Unity PF) Series Modular Double Conversion 3-Phase
Part Number | Model | Description | List Price
99000872 | M90-ENC (Unity PF) | Xtreme Power M90U (Unity PF) Series modular online 208/120 VAC three-phase UPS enclosure set up for internal battery. Includes 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; 2 Year Parts Warranty; Start-up and onsite labor is not included; 20.3" W x 39.4" D x 54.0" H. 474 lbs. Enclosure can accomodate up to 3 x 20k for 60KVA for 45KVA (or 3 x 15K for 45KVA) M90 (Unity PF) Power Modules and up to 12 M90 battery trays. Power modules and battery trays ordered seperately. | 14200
99000873 | M90L-ENC (Unity PF) | Xtreme Power M90U (Unity PF) Series modular online 208/120 VAC three-phase UPS enclosure set up for external battery (no internal batteries). Includes 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; 2 Year Parts Warranty; Start-up and onsite labor is not included; 20.3" W x 39.4" D x 30" H. 227 lbs. Enclosure can accomodate up to 3 x 20k for 60KVA (or 3 x 15K for 45KVA) M90U (Unity PF) Power Modules. Power modules and external battery ordered seperately. | 10300
99000870 | M90-PWRM (Unity PF) | Xtreme Power M90U Series 20kVA/20kW power module. 208/120 VAC three-phase; 19.5" W x 29.5" D x 5.5" H. 74 lbs. Unity PF | 8500
99000871 | M90-PWRM15 (Unity PF) | Xtreme Power M90U Series 15kVA/15kW power module. 208/120 VAC three-phase; 19.5" W x 29.5" D x 5.5" H. 73 lbs. Unity PF | 6700
90000563 | M90-BATT | Xtreme Power M90 battery tray for M90, M90U, M90-BOS. Includes (10) UPS 12580 batteries. Four (4) battery trays required for each 20kVA/18kW supported. __ Battery trays provide __ minutes runtime @ __KVA load. 2 year Warranty; 4,3" W x 28.5" D x 6.5" H; 68 lbs. | 890
90000885 | M90-BATT-EMPTY | Xtreme Power M90 empty battery tray for M90, M90U, M90-BOS. Includes battery interconnection cables. No batteries included. Minumum of four (4) battery trays required for each 20kVA/18kW supported. 4,3" W x 28.5" D x 6.5" H; 10 lbs. | 460
90000852 | M90-BOS | M90L Matching Battery Cabinet. Holds up to (12) M90-BATT battery trays. 20.3"W x 39.4"D x 30"H; 227 lbs. M90-BATT battery trays ordered seperately. | 5500
90000716 | M90-BC | External Modular Battery Cabinet. Holds up to 32 M90-BCBAT battery modules. 23.6"W x 43.8"D x 79.1"H; 416 lbs. Battery modules ordered seperately. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 12200
90000764 | M90-BCBAT | M90-BC Battery Module with (5)HR1290 batteries for M90-BC Battery Cabinet. 7.3"W x 38.5"D x 3.2"H; 85 lbs. Four modules required for each string. | 1025
90000851 | M90-BCBT | Empty Battery Tray for M90-BC External Battery Cabinet. 7.3"W x 38.5"D x 3.2"H; 14 lbs. Batteries ordered seperately. | 500
90000565 | M90 SKIRT | Xtreme Power M90(L) Skirt Kit. Installs between the UPS and floor to cover the casters and open space below UPS. Dims: TBD, 20 lbs. | 380
90000678 | M90-SEIS | Xtreme Power M90-ENC Seismic Anchor Kit. Includes Site Specific Seismic Calculations with State of California Engineer Stamp. Lead time 3-4 weeks ARO. Weight: 15 lbs. Requires site specific information to be submitted at time of order. One Kit required for each UPS. | 1900
| M90LU-SEIS | Xtreme Power M90L-ENC Seismic Anchor Kit. Includes Site Specific Seismic Calculations with State of California Engineer Stamp. Lead time 3-4 weeks ARO. Weight: 15 lbs. Requires site specific information to be submitted at time of order. One Kit required for each UPS . | 1900
| M90BC-SEIS | Xtreme Power M90-BC Seismic Anchor Kit. Includes Site Specific Seismic Calculations with State of California Engineer Stamp. Lead time 3-4 weeks ARO. Weight: 15 lbs. Requires site specific information to be submitted at time of order. One Kit required for each M90-BC battery cabinet. | 1900
M90 Bundles (with internal batteries)
Part Number | Model | Description | List Price
Bundle | M90U-15k04BM | Xtreme Power M90U Series 15KVA/15kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes one 15kVA/15kW power module; four (4) battery trays providing 9 minutes runtime at 15kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; 2 Year Parts Warranty; Start-up and onsite labor is not included; 20.3" W x 39.4" D x 54.0" H. 819 lbs. Enclosure can accommodate up to 2 additional 15k M90 (Unity PF) Power Modules and up to 8 additional M90 battery trays. | 24460
Bundle | M90U-15k06BM | Xtreme Power M90U Series 15KVA/15kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes one 15kVA/15kW power module; six (6) battery trays providing 16 minutes runtime at 15kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 955 lbs. Enclosure can accommodate up to 2 additional 15k M90 (Unity PF) Power Modules and up to 6 additional M90 battery trays. | 26240
Bundle | M90U-15k08BM | Xtreme Power M90U Series 15KVA/15kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes one 15kVA/15kW power module; eight (8) battery trays providing 22 minutes runtime at 15kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 1090 lbs. Enclosure can accommodate up to 2 additional 15k M90 (Unity PF)Power Modules and up to 4 additional M90 battery trays. | 28020
Bundle | M90U-15k10BM | Xtreme Power M90U Series 15KVA/15kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes one 15kVA/15kW power module; ten (10) battery trays providing 29 minutes runtime at 15kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 1225 lbs. Enclosure can accommodate up to 2 additional 15k M90 (Unity PF)Power Modules and up to 2 additional M90 battery trays. | 29800
Bundle | M90U-15k12BM | Xtreme Power M90U Series 15KVA/15kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes one 15kVA/15kW power module; twelve (12) battery trays providing 37 minutes runtime at 15kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 1361 lbs. Enclosure can accommodate up to 2 additional 15k M90 (Unity PF) Power Modules. | 31580
Bundle | M90U-20k04BM | Xtreme Power M90U Series 20KVA/20kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes one 20kVA/20kW power module; four (4) battery trays providing 6 minutes runtime at 20kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 820 lbs. Enclosure can accommodate up to 2 additional 20k M90 (Unity PF) Power Modules and up to 8 additional M90 battery trays. | 26260
Bundle | M90U-20k06BM | Xtreme Power M90U Series 20KVA/20kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes one 20kVA/20kW power module; x six (6) battery trays providing 11 minutes runtime at 20kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 956 lbs. Enclosure can accommodate up to 2 additional 20k M90 (Unity PF) Power Modules and up to 6 additional M90 battery trays. | 28040
Bundle | M90U-20k08BM | Xtreme Power M90U Series 20KVA/20kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes one 20kVA/20kW power module; eight (8) battery trays providing 16 minutes runtime at 20kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 1092 lbs. Enclosure can accommodate up to 2 additional 20k M90 (Unity PF) Power Modules and up to 4 additional M90 battery trays. | 29820
Bundle | M90U-20k10BM | Xtreme Power M90U Series 20KVA/20kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes one 20kVA/20kW power module; ten (10) battery trays providing 21 minutes runtime at 20kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 1228 lbs. Enclosure can accommodate up to 2 additional 20k M90 (Unity PF)Power Modules and up to 2 additional M90 battery trays. | 31600
Bundle | M90U-20k12BM | Xtreme Power M90U Series 20KVA/20kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes one 20kVA/20kW power module; twelve (12) battery trays providing 26 minutes runtime at 20kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Warranty; . 20.3" W x 39.4" D x 54.0" H. 1364 lbs. Enclosure can accommodate up to 2 additional 20k M90 (Unity PF) Power Modules. | 33380
Bundle | M90U-30k06BM | Xtreme Power M90U Series 30KVA/30kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes two 15kVA/15kW power modules; six (6) battery trays providing 6 minutes runtime at 30kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 1029 lbs. Enclosure can accommodate up to 1 additional 15k M90 (Unity PF)Power Module and up to 6 additional M90 battery trays. | 32940
Bundle | M90U-30k08BM | Xtreme Power M90U Series 30KVA/30kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes two 15kVA/15kW power modules; eight (8) battery trays providing 9 minutes runtime at 30kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 1165 lbs. Enclosure can accommodate up to 1 additional 15k M90 (Unity PF)Power Module and up to 4 additional M90 battery trays. | 34720
Bundle | M90U-30k10BM | Xtreme Power M90U Series 30KVA/30kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes two 15kVA/15kW power modules; ten (10) battery trays providing 12 minutes runtime at 30kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 1300 lbs. Enclosure can accommodate up to 1 additional 15k M90 (Unity PF) Power Module and up to 2 additional M90 battery trays. | 36500
Bundle | M90U-30k12BM | Xtreme Power M90U Series 30KVA/30kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes two 15kVA/15kW power modules; twelve (12) battery trays providing 16 minutes runtime at 30kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 1436 lbs. Enclosure can accommodate up to 1 additional 15k M90 (Unity PF) Power Module. | 38280
Bundle | M90U-40k08BM | Xtreme Power M90U Series 40KVA/40kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes two 20kVA/20kW power modules; eight (8) battery trays providing 6 minutes runtime at 40kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; . 20.3" W x 39.4" D x 54.0" H. 1166 lbs. Enclosure can accomodate 1 additional 20k M90 (Unity PF) Power Module and 4 additional battery trays. | 38320
Bundle | M90U-40k10BM | Xtreme Power M90U Series 40KVA/40kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes two 20kVA/20kW power modules; ten (10) battery trays providing 8 minutes runtime at 40kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; . 20.3" W x 39.4" D x 54.0" H. 1302 lbs. Enclosure can accomodate 1 additional 20k M90 (Unity PF) Power Module and 2 additional battery trays. | 40100
Bundle | M90U-40k12BM | Xtreme Power M90 Series 40KVA/40kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes two 20kVA/20kW power modules; twelve (12) battery trays providing 11 minutes runtime at 40kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; . 20.3" W x 39.4" D x 54.0" H. 1438 lbs. Enclosure can accommodate 1 additional 20k M90 (Unity PF) Power Module. | 41880
Bundle | M90U-45k08BM | Xtreme Power M90U Series 45KVA/45kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes three 15kVA/15kW power modules; eight (8) battery trays providing 5 minutes runtime at 45kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 1239 lbs. Enclosure can accommodate up to 4 additional M90 battery trays. | 41420
Bundle | M90U-45k10BM | Xtreme Power M90U Series 45KVA/45kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes three 15kVA/15kW power modules; ten (10) battery trays providing 7 minutes runtime at 45kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 1375 lbs. Enclosure can accommodate up to 2 additional M90 battery trays. | 43200
Bundle | M90U-45k12BM | Xtreme Power M90U Series 45KVA/45kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes three 15kVA/15kW power modules; twelve (12) battery trays providing 9 minutes runtime at 45kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 1511 lbs. | 44980
Bundle | M90U-60k10BM | Xtreme Power M90U Series 60KVA/60kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes three 20kVA/20kW power modules; ten (10) battery trays providing 4 minutes runtime at 60kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 1376 lbs. Enclosure can accommodate up to 2 additional M90 battery trays. | 48600
Bundle | M90U-60k12BM | Xtreme Power M90U Series 60KVA/60kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes three 20kVA/20kW power modules; twelve (12) battery trays providing 6 minutes runtime at 60kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 1512 lbs. | 50380
M90L Bundles (for use with external batteries)
Part Number | Model | Description | List Price
Bundle | M90LU-15k | Xtreme Power M90LU Series 15KVA/15kW modular online 208/120 VAC three-phase UPS enclosure set up for external batteries. Includes one 15kVA/15kW power module; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 30.0" H. 300 lbs. Enclosure can accommodate up to 2 additional 15k M90 (Unity PF) Power Modules. | 17000
Bundle | M90LU-20k | Xtreme Power M90LU Series 20KVA/20kW modular online 208/120 VAC three-phase UPS enclosure set up for external batteries. Includes one 20kVA/20kW power module; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 30.0" H. 301 lbs. Enclosure can accommodate up to 2 additional 20k M90 (Unity PF) Power Modules. | 18800
Bundle | M90LU-30k | Xtreme Power M90LU Series 30KVA/30kW modular online 208/120 VAC three-phase UPS enclosure set up for external batteries. Includes two 15kVA/15kW power modules; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 30.0" H. 373 lbs. Enclosure can accommodate up to one additional 15k M90 (Unity PF) Power Module. | 23700
Bundle | M90LU-40k | Xtreme Power M90LU Series 40KVA/40kW modular online 208/120 VAC three-phase UPS enclosure set up for external batteries. Includes two 20kVA/20kW power modules; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 30.0" H. 375 lbs. Enclosure can accommodate up to one additional 20k M90 (Unity PF) Power Module. | 27300
Bundle | M90LU-45k | Xtreme Power M90LU Series 45KVA/45kW modular online 208/120 VAC three-phase UPS enclosure set up for external batteries. Includes three 15kVA/15kW power modules; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 30.0" H. 446 lbs. | 30400
Bundle | M90LU-60k | Xtreme Power M90 Series 60KVA/60kW modular online 208/120 VAC three-phase UPS enclosure set up for external batteries. Includes three 20kVA/20kW power modules; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 30.0" H. 449 lbs. | 35800
External M90-BC Battery for use with M90L UPS
Part Number | Model | Description | List Price
Bundle | M90-BC-04B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (4) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 756 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 16300
Bundle | M90-BC-08B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (8) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 1096 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 20400
Bundle | M90-BC-12B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (12) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 1436 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 24500
Bundle | M90-BC-16B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (16) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 1776 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 28600
Bundle | M90-BC-20B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (20) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 2116 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 32700
Bundle | M90-BC-24B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (24) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 2456 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 36800
Bundle | M90-BC-28B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (28) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 2796 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 40900
Bundle | M90-BC-32B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (32) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Each battery string (4 modules) protected by a 100A breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 3136 lbs. Battery modules shipped on separate pallet. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 45000
External M90-BOS Battery for use with M90L UPS
Part Number | Model | Description | List Price
Bundle | M90-BOS-04B | M90L Matching Battery Cabinet with (4) M90-BATT battery trays. 20.3"W x 39.4"D x 30"H; 499 lbs. Can hold up to (8) additional M90-BATT battery trays. | 9060
Bundle | M90-BOS-06B | M90L Matching Battery Cabinet with (6) M90-BATT battery trays. 20.3"W x 39.4"D x 30"H; 635 lbs. Can hold up to (6) additional M90-BATT battery trays. | 10840
Bundle | M90-BOS-08B | M90L Matching Battery Cabinet with (8) M90-BATT battery trays. 20.3"W x 39.4"D x 30"H; 771 lbs. Can hold up to (4) additional M90-BATT battery trays. | 12620
Bundle | M90-BOS-10B | M90L Matching Battery Cabinet with (10) M90-BATT battery trays. 20.3"W x 39.4"D x 30"H; 907 lbs. Can hold up to (2) additional M90-BATT battery trays. | 14440
Bundle | M90-BOS-12B | M90L Matching Battery Cabinet with (12) M90-BATT battery trays. 20.3"W x 39.4"D x 30"H; 1043 lbs. | 16180
External Maintenance Bypass Options (wallmount)
Part Number | Model | Description | List Price
| 90885-C208310ECA060A06013MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 60 A, 10kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 22"W x 24"H x 9"D; 55 lbs. For Use with E91 15kVA and all M90 Family 15kVA UPS | Call For Price
| 90885-C208310ECA080A08013MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 60 A, 10kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 22"W x 24"H x 9"D; 55 lbs. For Use with E91 20kVA and all M90 Family 20kVA UPS | Call For Price
| 90880-C208322ECA125A12502MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 125 A, 22kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 30"W x 36"H x 10"D; 110 lbs. For Use with E91 30kVA and all M90 Family 30kVA UPS | Call For Price
| 90880-C208322ECA175A17502MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 175 A, 22kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 30"W x 36"H x 10"D; 110 lbs. For Use with all M90 Family up to 45kVA UPS | Call For Price
| 90881-C208365ECA250A25002MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 250 A, 65kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 30"W x 42"H x 11"D; 125 lbs. For Use with all M90 Family up to 60kVA | Call For Price
Note: | You can add 24V SKRU to 90880, 90881, and 90843 (not 90885) Series switches. You must replace the "02" in the P/N with "44" (example: 90880-C208322ECA150A15044MB, add SKRU adder to the list price, AND you must include a M90-COMM card to the UPS quote to interface with the MBP.
Contact XPC for MBS with distribution and/or transformer options.
Connectivity Options
Part Number | Model | Description | List Price
90000566 | SNMP-2P3 | Internal two port SNMP/WEB Card for use with E91, M90(U) and X90 Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-EMD Environmental Monitor; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 349
90000267 | MODBUS-IN | MODBUS CARD for use with the E91, M90(U) and X90 Series UPS; packaging = 7.25" x 6" x 2.5", 1 lbs | 319
90000398 | SNMP-EMD | Environmental Monitoring Sensor to monitor room temperature and humidity - used with SNMP-2P3 SNMP/WEB Card. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 180
90000498 | M90-COMM | Extra Communications card for M90. Allows for (6) programmable Form C relay contact outputs, (2) external Form C contact inputs, and up to (4) optional external temperature probe inputs and provides an additional card slot for Web/SNMP card . Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 370
| M90-BTS | Battery Temperature Sensor. Allows M90 and X90 Series UPS to monitor battery temperature and provide temperature compensated battery charging. A single temperature sensor can connect to temperature port on UPS chassis. Up to four additional temperature sensors can be connected with optional M90-COMM communication card. Temperature sensor has 3 meter cable. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 66
Service Options
Part Number | Model | Description | List Price
90000570 | M90SUS81 | M90, and M90L 5x8 Startup and 1 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes installation of the power modules and Internal battery trays, where applicable, by the Startup technician. | 4900
90000571 | M90SUS82 | M90, M90L, E90 and M90S 5x8 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes installation of the power modules and Internal battery trays, where applicable, by the Startup technician. | 5500
90000593 | M90SUS83 | M90, M90L, E90 and M90S 5x8 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes installation of the power modules and Internal battery trays, where applicable, by the Startup technician. | 8400
90000592 | M90SU7242 | M90, M90L, E90 and M90S 7x24 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes installation of the power modules and Internal battery trays, where applicable, by the Startup technician. | 7150
90000647 | M90SU7245 | M90, M90L, E90 and M90S Startup 7x24 and 5 year On-Site Warranty. For Zone 1 (within 100 miles of XPC Service Center). Does not include preventative maintenance visits. | 17900
90000594 | M90EXW1YR | M90, M90L, E90 and M90S One year extention of factory warranty. This warranty covers parts and depot repair labor. | 3200
90000648 | M90PM724 | M90, M90L, E90 and M90S Preventative Maintenance Service, 7x24. For Zone 1 (within 100 miles of XPC Service Center). | 4600
90000538 | SVCADD | Service adder for locations further than 100 miles. | 1050
90000730 | MSOS3BM | On-Site 3 Year Warranty for M90-BCBAT Battery Module. Three year coverage includes replacement parts and on-site corrective maintenance. Services are 5x8. Purchase one On-Site 3 Year Warranty Plan for each M90-BCBAT Battery Module. Startup with 3 year on-site must be purchased for the M90 UPS System. | 350
M90U-80 and M90U-140 Series (Unity PF) Modular Double Conversion Three-Phase Detailed Price Sheet
M90U-80 Series Ala Carte Solutions
99000874 | M90-ENC80 (Unity PF) | Xtreme Power M90U-80 Series (Unity PF) modular online 208/120 VAC three-phase UPS enclosure set up for internal or external battery (no internal batteries). Includes 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch , hot swappable internal batteries; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS, Energy Star; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 657 lbs. Enclosure can accomodate up to 4 x 15kVA or 20kVA M90 (Unity PF)Power Modules for up to 80KVA capacity and up to 16 x M90-80BAT battery modules. Power modules, internal battery modules and external battery ordered separately. | 20000
99000870 | M90-140-ENC (Unity PF) | Xtreme Power M90-140 Series (Unity PF) modular online 208/120 VAC three-phase UPS enclosure set up for external battery (no internal batteries). Includes 10" LCD touch screen, front mounted front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 657 lbs. Enclosure can accomodate up to 8 x 20kVA or 15kVA M90 (Unity PF) Power Modules for maximum 140KVA N+1 capacity. Power modules and external battery ordered separately. | 26000
99000870 | M90-PWRM (Unity PF) | Xtreme Power M90U Series 20kVA/20kW power module. 208/120 VAC three-phase; 19.5" W x 29.5" D x 5.5" H. 74 lbs. Unity PF | 8500
99000871 | M90-PWRM15 (Unity PF) | Xtreme Power M90U Series 15kVA/15kW power module. 208/120 VAC three-phase; 19.5" W x 29.5" D x 5.5" H. 73 lbs. Unity PF | 6700
90000763 | M90-80BAT | Internal Battery Module for M90-80 UPS. Contains (10) CSB 12580 Batteries each, 2 battery modules required per string, must be purchased in multiplies of 2, (xx) battery modules will provide __ minutes runtime @ ___kW load, Dims: 4.3"W x 28.5"D x 6.5"H, Weight 70 lbs. | 990
90000716 | M90-BC | M90-80 and M90-140 Matching External Modular Battery Cabinet. Holds up to (32) x M90-BCBAT Battery Modules; 2 Year Warranty, Dims 23.6"W x 43.3"D x 79.1"H, Weight 416 lbs. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 12200
90000764 | M90-BCBAT | Battery Module for M90-BC External Battery Cabinet. Contains (5) CSB HR1290 Batteries each, 4 battery modules required per string, must be purchased in multiplies of 4, (xx) battery modules will provide ___ minutes runtime @ ___kW load, Dims: 7.3"W x 38.5"D x 3.2"H, Weight 85 lbs. | 1025
90000850 | M90-80BT | Empty Battery Tray for M90-80. Each tray can hold 10 x 12V, 9AH batteries per tray. Two trays required for a full string. Dims; 4.3"H x 28.5" D x 6.5" H, 15 lbs. Includes battery to battery cabling. Batteries ordered seperately. | 500
90000851 | M90-BCBT | Empty Battery Tray for M90-BC. Each Tray can hold 5 x 12V, 20AH batteries per tray. Four trays required for a full string. Dims; 7.3"H x 38.5" D x 3.2" H, 14 lbs. Includes battery to battery cabling. Batteries ordered seperately. | 525
90000767 | M90-BUS | Bus Bar Kit for paralleled M90-BC External Battery Cabinets. Dims: 20"W x 4"D x 2.5"H, Weight 9 lbs. | 500
90001213 | M90-CBL | Cable kit for connecting M90-BC battery cabinet to M90U-140 or M90U-80 UPS. Includes 8’ cables and lugs. Pricing for longer length cables is available upon request. Quantity 2 required for M90U-140 UPS Systems. | 1050
| M90U80-SEIS | Xtreme Power M90-ENC80 Seismic Anchor Kit. Includes Site Specific Seismic Calculations with State of California Engineer Stamp. Lead time 3-4 weeks ARO. Weight: 15 lbs. Requires site specific information to be submitted at time of order. One Kit required for each UPS . | 1900
| M90U140-SEIS | Xtreme Power M90-ENC140 Seismic Anchor Kit. Includes Site Specific Seismic Calculations with State of California Engineer Stamp. Lead time 3-4 weeks ARO. Weight: 15 lbs. Requires site specific information to be submitted at time of order. One Kit required for each UPS . | 1900
| M90BC-SEIS | Xtreme Power M90-BC Seismic Anchor Kit. Includes Site Specific Seismic Calculations with State of California Engineer Stamp. Lead time 3-4 weeks ARO. Weight: 15 lbs. Requires site specific information to be submitted at time of order. One Kit required for each M90-BC battery cabinet. | 1900
M90U-80 Series UPS Bundled Solutions with 20kVA Unity PF Power Modules
Part Number | Model | Description | List Price
Bundle | M90U80-20K00B | Xtreme Power M90U-80 Series bundle; 20KVA/20KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (1) Power Module, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch ; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 731 lbs. Enclosure can accomodate up to 4 x 20kVA M90 Power Modules for 80KVA capacity. Power module(s) shipped on separate pallet. Additional power modules and external battery ordered separately. | 28500
Bundle | M90U80-20K04B | Xtreme Power M90U-80 Series bundle; 20KVA/20KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (1) Power Module, (4) M90-80BAT Battery Modules providing 6 minutes runtime at 20KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch ; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1011 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 32460
Bundle | M90U80-20K06B | Xtreme Power M90U-80 Series bundle; 20KVA/20KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (1) Power Module, (6) M90U-80BAT Battery Modules providing 11 minutes runtime at 20KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch ; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1151 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 34440
Bundle | M90U80-20K08B | Xtreme Power M90U-80 Series bundle; 20KVA/20KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (1) Power Module, (8) M90-80BAT Battery Modules providing 16 minutes runtime at 20KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch ; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1291 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 36420
Bundle | M90U80-20K10B | Xtreme Power M90U-80 Series bundle; 20KVA/20KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (1) Power Module, (10) M90-80BAT Battery Modules providing 21 minutes runtime at 20KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch ; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1431 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 38400
Bundle | M90U80-20K12B | Xtreme Power M90U-80 Series bundle; 20KVA/20KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (1) Power Module, (12) M90-80BAT Battery Modules providing 26 minutes runtime at 20KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch ; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1571 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 40380
Bundle | M90U80-20K14B | Xtreme Power M90U-80 Series bundle; 20KVA/20KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (1) Power Module, (14) M90-80BAT Battery Modules providing 31 minutes runtime at 20KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch ; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1711 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 42360
Bundle | M90U80-20K16B | Xtreme Power M90U-80 Series bundle; 20KVA/20KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (1) Power Module, (16) M90-80BAT Battery Modules providing 37 minutes runtime at 20KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch ; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1851 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity. Power and battery modules shipped on separate pallet. Additional power modules ordered separately. | 44340
Bundle | M90U80-40K00B | Xtreme Power M90U-80 Series bundle; 40KVA/40KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (2) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch ; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 805 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity. Power module(s) shipped on separate pallet. Additional power modules and external battery ordered separately. | 37000
Bundle | M90U80-40K08B | Xtreme Power M90U-80 Series bundle; 40KVA/40KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (2) Power Modules, (8) M90-80BAT Battery Modules providing 6 minutes runtime at 40kW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1365 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 44920
Bundle | M90U80-40K10B | Xtreme Power M90U-80 Series bundle; 40KVA/40KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (2) Power Modules, (10) M90-80BAT Battery Modules providing 8 minutes runtime at 40kW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1505 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 46900
Bundle | M90U80-40K12B | Xtreme Power M90U-80 Series bundle; 40KVA/40KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (2) Power Modules, (12) M90U-80BAT Battery Modules providing 11 minutes runtime at 40kW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1645 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 48880
Bundle | M90U80-40K14B | Xtreme Power M90U-80 Series bundle; 40KVA/40KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (2) Power Modules, (14) M90-80BAT Battery Modules providing 13 minutes runtime at 40kW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1785 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 50860
Bundle | M90U80-40K16B | Xtreme Power M90U-80 Series bundle; 40KVA/40KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (2) Power Modules, (16) M90-80BAT Battery Modules providing 13 minutes runtime at 40kW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1925 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity. Power and battery modules shipped on separate pallet. Additional power modules ordered separately. | 52840
Bundle | M90U80-60K00B | Xtreme Power M90U-80 Series bundle; 60KVA/60KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (3) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 879 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity. Power module(s) shipped on separate pallet. Additional power modules and external battery ordered separately. | 45500
Bundle | M90U80-60K10B | Xtreme Power M90U-80 Series bundle; 60KVA/60KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (3) Power Modules, (10) M90-80BAT Battery Modules providing 4 minutes runtime at 60kW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1579 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity and up to 16 battery modules for longer runtime.. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 55400
Bundle | M90U80-60K12B | Xtreme Power M90U-80 Series bundle; 60KVA/60KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (3) Power Modules, (12) M90-80BAT Battery Modules providing 6 minutes runtime at 60kW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1719 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity and up to 16 battery modules for longer runtime.. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 57380
Bundle | M90U80-60K14B | Xtreme Power M90U-80 Series bundle; 60KVA/60KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (3) Power Modules, (14) M90-80BAT Battery Modules providing 8 minutes runtime at 60kW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1859 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity and up to 16 battery modules for longer runtime.. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 59360
Bundle | M90U80-60K16B | Xtreme Power M90U-80 Series bundle; 60KVA/60KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (3) Power Modules, (16) M90-80BAT Battery Modules providing 9 minutes runtime at 60kW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1999 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity. Power and battery modules shipped on separate pallet. Additional power modules ordered separately. | 61340
Bundle | M90U80-80K00B | Xtreme Power M90U-80 Series bundle; 80KVA/80KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (4) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 953 lbs. Power module(s) shipped on separate pallet. External battery ordered separately. | 54000
Bundle | M90U80-80K14B | Xtreme Power M90U-80 Series bundle ; 80KVA/80KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (4) Power Modules, (14) M90-80BAT Battery Modules providing 4 minutes runtime at 80kW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1933 lbs. Enclosure can accomodate up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional battery modules ordered separately. | 67860
Bundle | M90U80-80K16B | Xtreme Power M90U-80 Series bundle ; 80KVA/80KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (4) Power Modules, (16) M90-80BAT Battery Modules providing 6 minutes runtime at 80kW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 2073 lbs. Power and battery modules shipped on separate pallet. | 69840
M90U-80 Series UPS Bundled Solutions W/ 15kVA Unity PF Power Modules
Bundle | M90U80-15k00B | Xtreme Power M90U-80 Series bundle; 15KVA/15KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (1) Power Module, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 730 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity. Power module(s) shipped on separate pallet. Additional power modules and external battery ordered separately. | 26700
Bundle | M90U80-15k04B | Xtreme Power M90U-80 Series bundle; 15KVA/15KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (1) Power Module, (4) M90-80BAT Battery Modules providing 9 minutes runtime at 15KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1010 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 30660
Bundle | M90U80-15k06B | Xtreme Power M90U-80 Series bundle; 15KVA/15KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (1) Power Module, (6) M90-80BAT Battery Modules providing 16 minutes runtime at 15KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1150 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 32640
Bundle | M90U80-15k08B | Xtreme Power M90U-80 Series bundle; 15KVA/15KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (1) Power Module, (8) M90-80BAT Battery Modules providing 22 minutes runtime at 15KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1290 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 34620
Bundle | M90U80-15k10B | Xtreme Power M90U-80 Series bundle; 15KVA/15KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (1) Power Module, (10) M90-80BAT Battery Modules providing 29 minutes runtime at 15KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1430 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 36600
Bundle | M90U80-15k12B | Xtreme Power M90U-80 Series bundle; 15KVA/15KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (1) Power Module, (12) M90-80BAT Battery Modules providing 37 minutes runtime at 15KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1570 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 38580
Bundle | M90U80-15k14B | Xtreme Power M90U-80 Series bundle; 15KVA/15KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (1) Power Module, (14) M90-80BAT Battery Modules providing 44 minutes runtime at 15KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1710 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 40560
Bundle | M90U80-15k16B | Xtreme Power M90U-80 Series bundle; 15KVA/15KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (1) Power Module, (16) M90-80BAT Battery Modules providing 52 minutes runtime at 15KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1850 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity. Power and battery modules shipped on separate pallet. Additional power modules ordered separately. | 42540
Bundle | M90U80-30k00B | Xtreme Power M90U-80 Series bundle; 30KVA/30KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (2) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 803 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity. Power module(s) shipped on separate pallet. Additional power modules and external battery ordered separately. | 33400
Bundle | M90U80-30k06B | Xtreme Power M90U-80 Series bundle; 30KVA/30KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (2) Power Modules, (6) M90-80BAT Battery Modules providing 6 minutes runtime at 30kW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1223 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 39340
Bundle | M90U80-30k08B | Xtreme Power M90U-80 Series bundle; 30KVA/30KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (2) Power Modules, (8) M90-80BAT Battery Modules providing 9 minutes runtime at 30KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1363 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 41320
Bundle | M90U80-30k10B | Xtreme Power M90U-80 Series bundle; 30KVA/30KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (2) Power Modules, (10) M90-80BAT Battery Modules providing 12 minutes runtime at 30KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1503 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 43300
Bundle | M90U80-30k12B | Xtreme Power M90U-80 Series bundle; 30KVA/30KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (2) Power Modules, (12) M90-80BAT Battery Modules providing 16 minutes runtime at 30KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1643 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 45280
Bundle | M90U80-30k14B | Xtreme Power M90U-80 Series bundle; 30KVA/30KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (2) Power Modules, (14) M90-80BAT Battery Modules providing 19 minutes runtime at 30KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1783 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 47260
Bundle | M90U80-30k16B | Xtreme Power M90U-80 Series bundle; 30KVA/30KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (2) Power Modules, (16) M90-80BAT Battery Modules providing 22 minutes runtime at 30KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1923 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity. Power and battery modules shipped on separate pallet. Additional power modules ordered separately. | 49240
Bundle | M90U80-45k00B | Xtreme Power M90U-80 Series bundle; 45KVA/45KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (3) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 876 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity. Power module(s) shipped on separate pallet. Additional power modules and external battery ordered separately. | 40100
Bundle | M90U80-45k08B | Xtreme Power M90U-80 Series bundle; 45KVA/45KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (3) Power Modules, (8) M90-80BAT Battery Modules providing 5 minutes runtime at 45KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1436 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 48020
Bundle | M90U80-45k10B | Xtreme Power M90U-80 Series bundle; 45KVA/45KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (3) Power Modules, (10) M90-80BAT Battery Modules providing 7 minutes runtime at 45KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1576 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 50000
Bundle | M90U80-45k12B | Xtreme Power M90U-80 Series bundle; 45KVA/45KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (3) Power Modules, (12) M90-80BAT Battery Modules providing 9 minutes runtime at 45KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1716 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 51980
Bundle | M90U80-45k14B | Xtreme Power M90U-80 Series bundle; 45KVA/45KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (3) Power Modules, (14) M90-80BAT Battery Modules providing 11 minutes runtime at 45KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1856 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 53960
Bundle | M90U80-45k16B | Xtreme Power M90U-80 Series bundle; 45KVA/45KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (3) Power Modules, (16) M90-80BAT Battery Modules providing 14 minutes runtime at 45KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1996 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity. Power and battery modules shipped on separate pallet. Additional power modules ordered separately. | 55940
Bundle | M90U80-60Ka00B | Xtreme Power M90U-80 Series bundle; 60KVA/60KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (4) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 949 lbs. Power module(s) shipped on separate pallet. | 46800
Bundle | M90U80-60Ka10B | Xtreme Power M90U-80 Series bundle; 60KVA/60KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (4) Power Modules, (10) M90-80BAT Battery Modules providing 4 minutes runtime at 60KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1889 lbs. Enclosure can accomodate up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional battery modules ordered separately. | 56700
Bundle | M90U80-60Ka12B | Xtreme Power M90U-80 Series bundle; 60KVA/60KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (4) Power Modules, (12) M90-80BAT Battery Modules providing 6 minutes runtime at 60KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 2029 lbs. Enclosure can accomodate up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional battery modules ordered separately. | 58680
Bundle | M90U80-60Ka14B | Xtreme Power M90U-80 Series bundle; 60KVA/60KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (4) Power Modules, (14) M90-80BAT Battery Modules providing 8 minutes runtime at 60KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 2169 lbs. Enclosure can accomodate up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional battery modules ordered separately. | 60660
Bundle | M90U80-60Ka16B | Xtreme Power M90U-80 Series bundle; 60KVA/60KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (4) Power Modules, (16) M90-80BAT Battery Modules providing 9 minutes runtime at 60KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 2309 lbs. Enclosure can accomodate up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. | 62640
M90U-140 Series UPS Bundled Solutions with 20kVA Unity PF Power Modules (no batteries)
Part Number | Model | Description | List Price
Bundle | M90U140-20K | Xtreme Power M90-140 Series bundle; 20KVA/20KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (1) Power Module, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 731 lbs. Enclosure can accomodate up to 8 x 20kVA M90 (Unity PF) Power Modules for 140KVA N+1 capacity. Power module(s) shipped on separate pallet. Additional power modules and external battery ordered separately. | 34500
Bundle | M90U140-40K | Xtreme Power M90-140 Series bundle; 40KVA/40KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (2) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 805 lbs. Enclosure can accomodate up to 8 x 20kVA M90 (Unity PF) Power Modules for 140KVA N+1 capacity. Power Modules shipped on separate pallet. Additional power modules and external battery ordered separately. | 43000
Bundle | M90U140-60K | Xtreme Power M90-140 Series bundle; 60KVA/60KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (3) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 879 lbs. Enclosure can accomodate up to 8 x 20kVA M90 (Unity PF) Power Modules for 140KVA N+1 capacity. Power Modules shipped on separate pallet. Additional power modules and external battery ordered separately. | 51500
Bundle | M90U140-80K | Xtreme Power M90-140 Series bundle; 80KVA/80KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (4) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 953 lbs. Enclosure can accomodate up to 8 x 20kVA M90 (Unity PF) Power Modules for 140KVA N+1 capacity. Power Modules shipped on separate pallet. Additional power modules and external battery ordered separately. | 60000
Bundle | M90U140-100K | Xtreme Power M90-140 Series bundle; 100KVA/100KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (5) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1027 lbs. Enclosure can accomodate up to 8 x 20kVA M90 (Unity PF) Power Modules for 140KVA N+1 capacity. Power Modules shipped on separate pallet. Additional power modules and external battery ordered separately. | 68500
Bundle | M90U140-120K | Xtreme Power M90-140 Series bundle; 120KVA/120KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (6) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1101 lbs. Enclosure can accomodate up to 8 x 20kVA M90 (Unity PF) Power Modules for 140KVA N+1 capacity. Power Modules shipped on separate pallet. Additional power modules and external battery ordered separately. | 77000
Bundle | M90U140-140K | Xtreme Power M90-140 Series bundle; 140KVA/140KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (7) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1175 lbs. Enclosure can accomodate up to 8 x 20kVA M90 (Unity PF) Power Modules for 140KVA N+1 capacity. Power Modules shipped on separate pallet. Additional power modules and external battery ordered separately. | 85500
Bundle | M90U140-140KN1 | Xtreme Power M90-140 Series bundle; 140KVA/140KW (N+1); Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (8) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1249 lbs. Power Modules shipped on separate pallet. External battery ordered separately. | 94000
M90U-140 Series UPS Bundled Solutions with 15kVA Unity PF Power Modules (no batteries)
Part Number | Model | Description | List Price
Bundle | M90U140-15K | Xtreme Power M90-140 Series bundle; 15KVA/15KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (1) Power Module, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 730 lbs. Enclosure can accomodate up to 8 x 15kVA M90 (Unity PF) Power Modules for 105KVA N+1 capacity. Power module(s) shipped on separate pallet. Additional power modules and external battery ordered separately. | 32700
Bundle | M90U140-30K | Xtreme Power M90-140 Series bundle; 30KVA/30KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (2) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 803 lbs. Enclosure can accomodate up to 8 x 15kVA M90 (Unity PF) Power Modules for 105KVA N+1 capacity. Power Modules shipped on separate pallet. Additional power modules and external battery ordered separately. | 39400
Bundle | M90U140-45K | Xtreme Power M90-140 Series bundle; 45KVA/45KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (3) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 876 lbs. Enclosure can accomodate up to 8 x 15kVA M90 (Unity PF) Power Modules for 105KVA N+1 capacity. Power Modules shipped on separate pallet. Additional power modules and external battery ordered separately. | 46100
Bundle | M90U140-60Ka | Xtreme Power M90-140 Series bundle; 60KVA/60KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (4) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 949 lbs. Enclosure can accomodate up to 8 x 15kVA M90 (Unity PF) Power Modules for 105KVA N+1 capacity. Power Modules shipped on separate pallet. Additional power modules and external battery ordered separately. | 52800
Bundle | M90U140-75K | Xtreme Power M90-140 Series bundle;75KVA/75KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (5) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1022 lbs. Enclosure can accomodate up to 8 x 15kVA M90 (Unity PF) Power Modules for 105KVA N+1 capacity. Power Modules shipped on separate pallet. Additional power modules and external battery ordered separately. | 59500
Bundle | M90U140-90K | Xtreme Power M90-140 Series bundle; 90KVA/90KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (6) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1095 lbs. Enclosure can accomodate up to 8 x 15kVA M90 (Unity PF) Power Modules for 105KVA N+1 capacity. Power Modules shipped on separate pallet. Additional power modules and external battery ordered separately. | 66200
Bundle | M90U140-105K | Xtreme Power M90-140 Series bundle; 105KVA/105KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (7) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1169 lbs. Enclosure can accomodate up to 8 x 15kVA M90 (Unity PF) Power Modules for 105KVA N+1 capacity. Power Modules shipped on separate pallet. Additional power modules and external battery ordered separately. | 72900
Bundle | M90U140-105KN1 | Xtreme Power M90-140 Series bundle; 105KVA/105KW N+1; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (7) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1242 lbs. Power Modules shipped on separate pallet. External battery ordered separately. | 79600
M90-BC Modular Battery Cabinet Bundles
Part Number | Model | Description | List Price
Bundle | M90-BC-04B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (4) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 756 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 16300
Bundle | M90-BC-08B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (8) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 1096 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 20400
Bundle | M90-BC-12B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (12) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 1436 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 24500
Bundle | M90-BC-16B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (16) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 1776 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 28600
Bundle | M90-BC-20B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (20) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 2116 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 32700
Bundle | M90-BC-24B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (24) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 2456 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 36800
Bundle | M90-BC-28B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (28) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 2796 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 40900
Bundle | M90-BC-32B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (32) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Each battery string (4 modules) protected by a 100A breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 3136 lbs. Battery modules shipped on separate pallet. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 45000
External Maintenance Bypass Options
Part Number | Model | Description | List Price
| 90881-C208365ECA250A25002MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 250 A, 65kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 30"W x 42"H x 11"D; 125 lbs. For Use with all M90 Family up to 60kVA | Call For Price
| 90881-C208365ECA300A30002MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 300 A, 65kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 30"W x 42"H x 11"D; 125 lbs. For Use with all M90 Family up to 75kVA | Call For Price
| 90881-C208365ECA350A35002MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 350 A, 65kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 30"W x 42"H x 11"D; 125 lbs. For Use with all M90 Family up to 80kVA | Call For Price
| 90881-C208365ECA400A40002MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 400 A, 65kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 30"W x 42"H x 11"D; 125 lbs. For Use with all M90 Family up to 105kVA | Call For Price
| 90882-C208365ECA500A50002MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 500 A, 65kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 36"W x 48"H x 13.5"D; 165 lbs. For Use with all M90 Family up to 120kVA | Call For Price
| 90882-C208365ECA600A60002MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 600 A, 65kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 36"W x 48"H x 13.5"D; 165 lbs. For Use with all M90 Family up to 140kVA | Call For Price
Contact XPC for MBS with distribution and/or transformer options.
Connectivity Options
Part Number | Model | Description | List Price
90000566 | SNMP-2P3 | Internal two port SNMP/WEB Card for use with E91, M90(U) and X90 Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-EMD Environmental Monitor; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 349
90000267 | MODBUS-IN | MODBUS CARD for use with the E91, M90(U) and X90 Series UPS; packaging = 7.25" x 6" x 2.5", 1 lbs | 319
90000398 | SNMP-EMD | Environmental Monitoring Sensor to monitor room temperature and humidity - used with SNMP-2P3 SNMP/WEB Card. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 180
90000498 | M90-COMM | Extra Communications card for M90. Allows for (6) programmable Form C relay contact outputs, (2) external Form C contact inputs, and up to (4) optional external temperature probe inputs and provides an additional card slot for Web/SNMP card . Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 370
| M90-BTS | Battery Temperature Sensor. Allows M90 and X90 Series UPS to monitor battery temperature and provide temperature compensated battery charging. A single temperature sensor can connect to temperature port on UPS chassis. Up to four additional temperature sensors can be connected with optional M90-COMM communication card. Temperature sensor has 3 meter cable. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 66
Service Options
Part Number | Model | Description | List Price
90000768 | M90814SU581 | M90-80 and M90-140 5x8 Startup and 1 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center) StartUP includes installation of the M90 power modules and Internal battery trays by the startup technician. | 5900
90000769 | M90814SU582 | M90-80 and M90-140 5x8 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes installation of the M90 power modules and Internal battery trays by the startup technician. | 6500
90000770 | M90814SU583 | M90-80 and M90-140 5x8 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes installation of the M90 power modules and Internal battery trays by the startup technician. | 9600
90000772 | M90814SU72 | M90-80 and M90-140 7x24 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes installation of the M90 power modules and Internal battery trays by the startup technician. | 8450
90000773 | M90814SU73 | M90-80 and M90-140 7x24 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes installation of the M90 power modules and Internal battery trays by the startup technician. | 11700
90000774 | M90814EX1 | M90-80 and M90-140 One year extention of factory warranty. This warranty covers parts and depot repair labor, extending standard factory warranty to 3yrs. | 4200
90000775 | M90814PM7 | M90-80 and M90-140 Preventative Maintenance Service, 7x24. For Zone 1 (within 100 miles of XPC Service Center). | 4900
90000730 | MSOS3BM | On-Site 3 Year Warranty for M90-BCBAT Battery Module. Three year coverage includes replacement parts and on-site corrective maintenance. Services are 5x8. Purchase one On-Site 3 Year Warranty Plan for each M90-BCBAT Battery Module. Startup with 3 year on-site must be purchased for the M90 UPS System. | 350
90000538 | SVCADD | Service adder for locations further than 100 miles. | 1050
X90 1-Slot & 2-Slot 50-140kVA
X90-1S & 2S Series Ala Carte Solutions
Part Number | Model | Description | List Price
90001316 | X90-ENC1S | X90-1S Series (Unity PF) modular online 480VAC three-phase, 3-wire top entry UPS enclosure set up for internal and/or external battery (no internal batteries included). Includes 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 58"H; 357 lbs. Enclosure can accommodate 1 x 50kVA/kW or 70kVA/kW X90 Power Modules for up to 70KVA/kW capacity and up to 16 x X90-BCBAT battery modules. Power module, internal battery modules and external battery ordered separately. | 29200
90001013 | X90-ENC2S | X90-2S Series (Unity PF) modular online 480VAC three-phase, 3-wire top entry UPS enclosure set up for internal and/or external battery (no internal batteries included). Includes 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 79"H; 657 lbs. Enclosure can accommodate up to 2 x 50kVA/kW or 70kVA/kW X90 Power Modules for up to 140KVA/kW capacity and up to 20 x X90-BCBAT battery modules. Power modules, internal battery modules and external battery ordered separately. | 35700
90001016 | X90-2SPM50 | Xtreme Power X90 50kVA/50kW power module. 480 VAC three-phase; 19.5" W x 29.5" D x 5.5" H. 104 lbs. | 9600
90001017 | X90-2SPM70 | Xtreme Power X90 Series 70kVA/70kW power module. 208/120 VAC three-phase; 19.5" W x 29.5" D x 5.5" H. 105 lbs. | 10500
90001066 | X90-BC | X90 Matching External Modular Battery Cabinet. Holds up to (36) x X90-BCBAT Battery Modules; 2 Year Warranty, Dims 23.6"W x 42"D x 79"H, Weight 416 lbs. | 6500
90001067 | X90-BCBAT | Battery Module for X90-2S Internal or X90-BC External Battery Cabinet. Contains (10) CSB 12580 Batteries each, 4 battery modules required per string, must be purchased in multiplies of 4, (xx) battery modules will provide ___ minutes runtime @ ___kW load, Dims: 4.3"W x 28.5"D x 6.5"H, Weight 70 lbs. | 1090
90001076 | X90-BCBT | Empty Battery Tray for X90-2S or X90-BC. Each Tray can hold (10) CSB 12580 batteries per tray. Four trays required for a full string. Dims; 4.3"W x 28.5"D x 6.5"H, 15 lbs. Includes battery to battery cabling. Batteries ordered separately. | 500
90001071 | X90-SC2S | Side car for bottom entry. Dims: 6.1"W x 42"D x 79"H | 900
90001075 | X90-SEIS | Xtreme Power X90-2S Seismic Anchor Kit. Includes Site Specific Seismic Calculations with State of California Engineer Stamp. Lead time 3-4 weeks ARO. Weight: TBD lbs. Requires site specific information to be submitted at time of order. One Kit required for each X90-2S UPS. | 1900
| X90BC-SEIS | Xtreme Power X90-BC Seismic Anchor Kit. Includes Site Specific Seismic Calculations with State of California Engineer Stamp. Lead time 3-4 weeks ARO. Weight: TBD lbs. Requires site specific information to be submitted at time of order. One Kit required for each X90-BC battery cabinet. | 1900
X90-1S Series UPS Bundled Solutions with 50kVA Unity PF Power Modules
Part Number | Model | Description | List Price
Bundle | X901S-50K00B | Xtreme Power X90-1S Series bundle; 50KVA/50KW; Modular online 480VAC three-phase, 3-Wire top entry UPS set up for external battery (no internal batteries). Includes (1) Power Module, static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 58"H; 461 lbs. Enclosure can accommodate 1 x 50kVA/kW or 70kVA/kW X90 Power Modules for up to 70KVA/kW capacity and up to 16 x X90-BCBAT battery modules External battery ordered separately. Power Module ships on a separate pallet. | 38800
Bundle | X901S-50K12B | Xtreme Power X90-1S Series bundle; 50KVA/50KW; Modular online 480VAC three-phase, 3-Wire top entry UPS. Includes (1) Power Module, (12) X90-BCBAT providing approximately 7 minutes at 50kW load; static switch,10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 58"H; 1301 lbs. Enclosure can accommodate 1 x 50kVA/kW or 70kVA/kW X90 Power Modules for up to 70KVA/kW capacity and up to 16 x X90-BCBAT battery modules Power and Battery Modules ship on a separate pallet. | 51880
Bundle | X901S-50K16B | Xtreme Power X90-1S Series bundle; 50KVA/50KW; Modular online 480VAC three-phase, 3-Wire top entry UPS. Includes (1) Power Module, (16) X90-BCBAT providing approximately 11 minutes at 50kW load, static switch; 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 58"H; 1581 lbs. Enclosure can accommodate 1 x 50kVA/kW or 70kVA/kW X90 Power Modules for up to 70KVA/kW capacity and up to 16 x X90-BCBAT battery modules. Power and Battery Modules ship on a separate pallet. | 56240
X90-1S Series UPS Bundled Solutions with 70kVA Unity PF Power Modules
Part Number | Model | Description | List Price
Bundle | X901S-70k00B | Xtreme Power X90-1S Series bundle; 70KVA/70KW; Modular online 480VAC three-phase, 3-Wire top entry UPS set up for external battery (no internal batteries). Includes (1) Power Module, static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 58"H; 462 lbs. Enclosure can accommodate 1 x 50kVA/kW or 70kVA/kW X90 Power Modules for up to 70KVA/kW capacity and up to 16 x X90-BCBAT battery modules. Internal battery modules and external battery ordered separately. Power Module ships on a separate pallet. | 39700
Bundle | X901S-70k16B | Xtreme Power X90-1S Series bundle; 70KVA/70KW; Modular online 480VAC three-phase, 3-Wire top entry UPS. Includes (1) Power Module, (16) X90-BCBAT providing approximately 7 minutes at 70kW load; static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty is included; 23.6"W x 42"D x 58"H; 1582 lbs. Enclosure can accommodate 1 x 50kVA/kW or 70kVA/kW X90 Power Modules for up to 70KVA/kW capacity and up to 16 x X90-BCBAT battery modules. Power and Battery Modules ship on a separate pallet. | 57140
X90-2S Series UPS Bundled Solutions with 50kVA Unity PF Power Modules
Part Number | Model | Description | List Price
Bundle | X902S-50K00B | Xtreme Power X90-2S Series bundle; 50KVA/50KW; Modular online 480VAC three-phase, 3-Wire top entry UPS set up for external battery (no internal batteries). Includes (1) Power Module, static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 79"H; 761 lbs. Enclosure can accommodate up to 2 x 50kVA/kW X90 Power Modules for up to 100KVA/kW capacity and up to 20 x X90-BCBAT battery modules. External battery ordered separately. Power Modules ship on a separate pallet. | 45300
Bundle | X902S-50K12B | Xtreme Power X90-2S Series bundle; 50KVA/50KW; Modular online 480VAC three-phase, 3-Wire top entry UPS. Includes (1) Power Module, (12) X90-BCBAT providing approximately 8 minutes at 50kW load; static switch,10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 79"H; 1601 lbs. Enclosure can accommodate up to 2 x 50kVA/kW X90 Power Modules for up to 100KVA/kW capacity and up to 20 x X90-BCBAT battery modules. Power and Battery Modules ship on a separate pallet. | 28380
Bundle | X902S-50K16B | Xtreme Power X90-2S Series bundle; 50KVA/50KW; Modular online 480VAC three-phase, 3-Wire top entry UPS. Includes (1) Power Module, (16) X90-BCBAT providing approximately 12 minutes at 50kW load, static switch; 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 79"H; 1881 lbs. Enclosure can accommodate up to 2 x 50kVA/kW X90 Power Modules for up to 100KVA/kW capacity and up to 20 x X90-BCBAT battery modules. Power and Battery Modules ship on a separate pallet. | 62740
Bundle | X902S-50K20B | Xtreme Power X90-2S Series bundle; 50KVA/50KW; Modular online 480VAC three-phase, 3-Wire top entry UPS. Includes (1) Power Module, (20) X90-BCBAT providing approximately 16 minutes at 50kW load; static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 79"H; 2161 lbs. Enclosure can accommodate up to 2 x 50kVA/kW X90 Power Modules for up to 100KVA/kW capacity and up to 20 x X90-BCBAT battery modules. Power and Battery Modules ship on a separate pallet. | 67100
Bundle | X902S-100K00B | Xtreme Power X90-2S Series bundle; 100KVA/100KW; Modular online 480VAC three-phase, 3-Wire top entry UPS set up for external battery (no internal batteries). Includes (2) Power Modules, static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 79"H; 865 lbs. Enclosure can accommodate up to 20 x X90-BCBAT battery modules. External battery cabinet ordered separately. Power Modules ship on a separate pallet. | 54900
Bundle | X902S-100K20B | Xtreme Power X90-2S Series bundle; 100KVA/100KW; Modular online 480VAC three-phase, 3-Wire top entry UPS. Includes (2) Power Module, (20) X90-BCBAT providing approximately 6 minutes at 100kW load; static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 79"H; 2265 lbs. Power and Battery Modules ship on a separate pallet. | 76700
X90-2S Series UPS Bundled Solutions W/ 70kVA Unity PF Power Modules
Bundle | X902S-70k00B | Xtreme Power X90-2S Series bundle; 70KVA/70KW; Modular online 480VAC three-phase, 3-Wire top entry UPS set up for external battery (no internal batteries). Includes (1) Power Module, static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 79"H; 762 lbs. Enclosure can accommodate up to 2 x 70kVA/kW X90 Power Modules for up to 140KVA/kW capacity and up to 20 x X90-BCBAT battery modules. External battery ordered separately. Power Modules ship on a separate pallet. | 46200
Bundle | X902S-70k16B | Xtreme Power X90-2S Series bundle; 70KVA/70KW; Modular online 480VAC three-phase, 3-Wire top entry UPS. Includes (1) Power Module, (16) X90-BCBAT providing approximately 8 minutes at 70kW load; static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty is included; 23.6"W x 42"D x 79"H; 1882 lbs. Enclosure can accommodate up to 2 x 70kVA/kW X90 Power Modules for up to 140KVA/kW capacity and up to 20 x X90-BCBAT battery modules. Power and Battery Modules ship on a separate pallet. | 63640
Bundle | X902S-70k20B | Xtreme Power X90-2S Series bundle; 70KVA/70KW; Modular online 480VAC three-phase, 3-Wire top entry UPS. Includes (1) Power Module, (20) X90-BCBAT providing approximately 10 minutes at 70kW load; static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 79"H; 2162 lbs. Enclosure can accommodate up to 2 x 70kVA/kW X90 Power Modules for up to 140KVA/kW capacity and up to 20 x X90-BCBAT battery modules. Power and Battery Modules ship on a separate pallet. | 68000
Bundle | X902S-140k00B | Xtreme Power X90-2S Series bundle; 140KVA/140KW; Modular online 480VAC three-phase, 3-Wire top entry UPS set up for external battery (no internal batteries). Includes (2) Power Modules, static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 79"H; 867 lbs. Enclosure can accommodate up to 20 x X90-BCBAT battery modules. External battery cabinet ordered separately. Power Modules ship on a separate pallet. | 56700
Bundle | X902S-140k28B | Xtreme Power X90-2S Series bundle; 140KVA/140KW; Modular online 480VAC three-phase, 3-Wire top entry UPS. Includes (2) Power Modules, X90-BC with (28) X90-BCBAT providing approximately 6 minutes at 140kW load; static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; UPS and Battery cabinet each 23.6"W x 42"D x 79"H; UPS 867lbs, X90-BC 2376lbs. Power and Battery Modules ship on a separate pallet. Qty 28 open battery slots for runtime expansion. | 93720
Bundle | X902S-140k36B | Xtreme Power X90-2S Series bundle; 140KVA/140KW; Modular online 480VAC three-phase, 3-Wire top entry UPS. Includes (2) Power Modules, X90-BC, (36) X90-BCBAT providing approximately 8 minutes at 140kW load; static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; UPS and Battery cabinet each 23.6"W x 42"D x 79"H; UPS 867 lbs, X90-BC 2936 lbs. Power and Battery Modules ship on a separate pallet. Qty 20 open battery slots for runtime expansion. | 102440
Bundle | X902S-140k40B | Xtreme Power X90-2S Series bundle; 140KVA/140KW; Modular online 480VAC three-phase, 3-Wire top entry UPS. Includes (2) Power Modules, X90-BC, (40) X90-BCBAT providing approximately 10 minutes at 140kW load; static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; UPS and Battery cabinet each 23.6"W x 42"D x 79"H; UPS 1147 lbs, X90-BC 2936 lbs. Power and Battery Modules ship on a separate pallet. Qty 16 open battery slots for runtime expansion. | 106880
Bundle | X902S-140k48B | Xtreme Power X90-2S Series bundle; 140KVA/140KW; Modular online 480VAC three-phase, 3-Wire top entry UPS. Includes (2) Power Modules, X90-BC, (48) X90-BCBAT providing approximately 12 minutes at 140kW load; static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; UPS and Battery cabinet each 23.6"W x 42"D x 79"H; UPS 1707 lbs, X90-BC 2936 lbs. Power and Battery Modules ship on a separate pallet. Qty 8 open battery slots for runtime expansion. | 115520
Bundle | X902S-140k56B | Xtreme Power X90-2S Series bundle; 140KVA/140KW; Modular online 480VAC three-phase, 3-Wire top entry UPS. Includes (2) Power Modules, X90-BC, (56) X90-BCBAT providing approximately 15 minutes at 140kW load; static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; UPS and Battery cabinet each 23.6"W x 42"D x 79"H; UPS 2265 7lbs, X90-BC 2936 lbs. Power and Battery Modules ship on a separate pallet. | 124240
X90-BC Modular Battery Cabinet Bundles
Part Number | Model | Description | List Price
Bundle | X90BC-04B | Xtreme Power X90-BC Modular Battery Cabinet bundle. Includes X90-BC Battery Cabinet and (4) X90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accommodate up to 36 battery modules for longer runtime. Battery modules must be added in sets of four. Battery Cabinet protected by a breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 42"D x 79"H; 696lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled. | 10860
Bundle | X90BC-08B | Xtreme Power X90-BC Modular Battery Cabinet bundle. Includes X90-BC Battery Cabinet and (8) X90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accommodate up to 36 battery modules for longer runtime. Battery modules must be added in sets of four. Battery Cabinet protected by a breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 42"D x 79"H; 976lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled. | 15220
Bundle | X90BC-12B | Xtreme Power X90-BC Modular Battery Cabinet bundle. Includes X90-BC Battery Cabinet and (12) X90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accommodate up to 36 battery modules for longer runtime. Battery modules must be added in sets of four. Battery Cabinet protected by a breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 42"D x 79"H; 1256lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled. | 19580
Bundle | X90BC-16B | Xtreme Power X90-BC Modular Battery Cabinet bundle. Includes X90-BC Battery Cabinet and (16) X90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accommodate up to 36 battery modules for longer runtime. Battery modules must be added in sets of four. Battery Cabinet protected by a breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ;23.6"W x 42"D x 79"H; 1536lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled. | 23940
Bundle | X90BC-20B | Xtreme Power X90-BC Modular Battery Cabinet bundle. Includes X90-BC Battery Cabinet and (20) X90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accommodate up to 36 battery modules for longer runtime. Battery modules must be added in sets of four. Battery Cabinet protected by a breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 42"D x 79"H; 1816lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled. | 28300
Bundle | X90BC-24B | Xtreme Power X90-BC Modular Battery Cabinet bundle. Includes X90-BC Battery Cabinet and (24) X90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accommodate up to 36 battery modules for longer runtime. Battery modules must be added in sets of four. Battery Cabinet protected by a breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 42"D x 79"H; 2096lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled. | 32660
Bundle | X90BC-28B | Xtreme Power X90-BC Modular Battery Cabinet bundle. Includes X90-BC Battery Cabinet and (28) X90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accommodate up to 36 battery modules for longer runtime. Battery modules must be added in sets of four. Battery Cabinet protected by a breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 42"D x 79"H; 2376lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled. | 37020
Bundle | X90BC-32B | Xtreme Power X90-BC Modular Battery Cabinet bundle. Includes X90-BC Battery Cabinet and (32) X90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accommodate up to 36 battery modules for longer runtime. Battery modules must be added in sets of four. Battery Cabinet protected by a breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 42"D x 79"H; 2656lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled. | 41380
Bundle | X90BC-36B | Xtreme Power X90-BC Modular Battery Cabinet bundle. Includes X90-BC Battery Cabinet and (36) X90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Battery modules must be added in sets of four. Battery Cabinet protected by a breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 42"D x 79"H; 2936lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled. | 45740
Connectivity Options
Part Number | Model | Description | List Price
90001245 | SNMP-2PG1 | Internal two port SNMP/WEB Card for use with X90, M90C, M90, M90L E91, and M90S Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-TMPH temperature and humidity probe; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 715
90000267 | MODBUS-IN | MODBUS CARD for use with the E91, M90(U) and X90 Series UPS; packaging = 7.25" x 6" x 2.5", 1 lbs | 319
90000398 | SNMP-TMPH | Temperature and humidity Probe - used with SNMP-2PG1 SNMP/WEB Card. Packaging = 7.25"W x 6.0"D x 2.5"H, 1.0 lbs | 329
| M90-BTS | Battery Temperature Sensor. Allows M90 and X90 Series UPS to monitor battery temperature and provide temperature compensated battery charging. A single temperature sensor can connect to temperature port on UPS chassis. Up to four additional temperature sensors can be connected with optional M90-COMM communication card. Temperature sensor has 3 meter cable. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 66
Service Options
Part Number | Model | Description | List Price
90001248 | X902SSU583 | Upgrade standard warranty to 3 years. Includes (1) PM (5x8) to be performed at beginning of year three. Must be purchased concurrently with equipment. Zone 1 - within 100 miles of XPC Service Center. | 6500
90001249 | X902SSU72 | Upgrade standard warranty to include 7x24 coverage. Must be purchased concurrently with equipment. Zone 1 - within 100 miles of XPC Service Center. | 2800
90001250 | X902SSU73 | Upgrade standard warranty to 3 years and 7x24 coverage. Includes (1) PM (7x24) to be performed at beginning of year three. Must be purchased concurrently with equipment. Zone 1 - within 100 miles of XPC Service Center. | 9300
90001251 | X902S1YREE | X90 One-year extension of factory on-site warranty, electronics only. This warranty covers parts and labor, extending standard factory warranty by 1yr. Includes (1) PM (7x24) to be performed at beginning of the extension year. Maximum of 5 years. | 8800
90001252 | X902SPM7 | X90-2S Preventative Maintenance Service, 7x24. For Zone 1 (within 100 miles of XPC Service Center). | 5800
90000538 | SVCADD | Service adder for locations further than 100 miles. | 1200
SPDU SERIES
Switched and Metered PDU
Part Number | Model | Description | List Price
90001340 | SPDU-0615C | Xtreme Power Switched and Metered-by-Outlet Power Distribution Unit (SPDU) with C14 power inlet and detachable 6-ft 5-15P to C13 power cord; (6) NEMA 5-15R outlets, each individually monitored and remotely controlled via integrated SNMP network interface and management software; Front-panel LCD displays outlet status, load, and temperature data. Includes 1080 J surge protection and built-in temperature sensor. 5-Year Warranty (USA & Canada). Certifications: UL 62368-1, CSA C22.2 No. 62368-1, UL 1449 Ed. 5, FCC Class B, TAA Compliant; 17.3″ W × 2.8″ D × 1.73″ H, 2.3 lbs. | 725
90001341 | SPDU-1415C | Xtreme Power Switched and Metered-by-Outlet Power Distribution Unit (SPDU) with C14 power inlet and detachable 6-ft 5-15P to C13 power cord; (14) NEMA 5-15R outlets, each individually monitored and remotely controlled via integrated SNMP network interface and management software; Front-panel LCD displays outlet status, load, and temperature data. Includes 3240 J surge protection and built-in temperature sensor. 5-Year Warranty (USA & Canada). Certifications: UL 62368-1, CSA C22.2 No. 62368-1, UL 1449 Ed. 5, FCC Class B, TAA Compliant; 17.3″ W × 3.5″ D × 3.5″ H, 5.4 lbs. | 950
XPDU SERIES
Switched PDU
Part Number | Model | Description | List Price
90000460 | SPD-0215 | Xtreme Power XPDU Series Switched Power PDU with C14 Power inlet with removeable 5-15P to C13 power cord; (2) 5-15/20R output receptacles each independently power controlled via included SNMP Port and Software; 2-Year Warranty; 6"W x 6.8"D x 1.9"H, 2.0 lbs | 519
90000765 | J40SP | Xtreme Power XPDU Series, Ultra Slim Switched Power PDU with IEC-C14 Inlet (optional line cords available). (3) 5-15R output receptacles each independently power controlled via included RJ45 SNMP Port and Software; Pass through RJ45 Port enables connection of additional network devices; Easy to read LED display shows on/off condition of individual receptacles; 3-Year Warranty; 8.07W"W x 7.28"D x 1.22"H, 3.25 lbs | 549
| XPC-515P-3RA | Optional 3 ft, 5-15P line cord with right angle offset for use with J40 series PDU. .5 lbs | 22
| XPC-515P-6RA | Optional 6ft, 5-15P line cord with right angle offset for use with J40 series PDU. .5 lbs | 22
Transformer PDU
Part Number | Model | Description | List Price
900007742 | JX-200 | J60 200W Isolation Transformer, 120 VAC, 50/60Hz, C14 inlet with removeable 5-15P line cord; (3) 5-15R output receptacles; 5A output breaker; complete line isolation; Common Mode and Normal Mode noise filtering; 300 joules surge suppression; UL16950, RoHS; 5-Year Full Warranty; 6.9" W x 8.5" D x 1.25" H; 6.6 lbs. | 220
90000739 | XPD-IT15A | Xtreme Power XPDU Series PDU with Isolation Transformer. 1500W, 208V in, 120V out. IEC-C14 inlet with 3' 5-15 line cord ; (16) 5-15R output receptacles protected by 15A breaker; 3-Year Warranty; 17.5"W x 15"D x 3.5"H (2U), 43 lbs. | 980
90000407 | XPD-IT60A | Xtreme Power XPDU Series 6KVA PDU with Isolation Transformer for use with P80G-5000 or P91 5-10K UPS. 6000W, 208 or 240 in, 208/104V or 240/120V out. 3ft L6-30P Input Cord. (1) L6-30R and (12) 5-15-20R output receptacles; rear panel 208/240 voltage selection switch; includes front panel rackmount brackets; ROHS Approved; 3-Year Warranty; 17.3"W x 18"D x 3.5"H (2U), 137 lbs. | 1750
90000781 | XPD-IT6KW | 6kVA PDU with Isolation Transformer 208V to 240/120V (or 240V to 240/120V), Input terminal bock, Output terminal block + (2) L14-30R and (8) 5–15/20R receptacles; 17.3”W x 31.8”D x 5.2”H; 122 lbs. | 2310
90000740 | XPD-IT10KW | 10kVA PDU with Isolation Transformer 208V to 240/120V (or 240V to 240/120V), Input terminal bock, Output terminal block + (2) L14-30R and (8) 5–15/20R receptacles; 17.3”W x 31.8”D x 5.2”H; 122 lbs. | 2760
Basic PDU 10A Models
Part Number | Model | Description | List Price
90000463 | J40 | Xtreme Power XPDU; ultra slim 120VAC, 10 Amp PDU with IEC-C14 Inlet (optional line cords available). (3) 5-15R output receptacles; Power reset button for manual recycling of power. 2400 Joules surge protection; 3-Year Warranty; 8.07W"W x 3.35"D x 1.22"H, 2 lbs | 210
90000466 | J40i | Xtreme Power XPDU; ultra slim 230 VAC, 10 Amp PDU with IEC-C14 Inlet (optional line cords available). (3) IEC C13 output receptacles; Power reset button for manual recycling of power. 2400 Joules surge protection; 3-Year Warranty; 8.07W"W x 3.35"D x 1.22"H, 2 lbs | 210
| XPC-515P-3RA | Optional 3 ft, 5-15P line cord with right angle offset for use with J40 series PDU. .5 lbs | 22
| XPC-515P-6RA | Optional 6ft, 5-15P line cord with right angle offset for use with J40 series PDU. .5 lbs | 22
Basic PDU 15A & 20A Models
Part Number | Model | Description | List Price
90000040 | XPD815HV | Xtreme Power XPDU Series Basic Power PDU with 12' Input line cord with 5-15P plug; (8) 5-15R output receptacles on rear of PDU; UL60950-1/cUL/FCC Approved; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 2.6 lbs | 120
90000041 | XPD1415HV | Xtreme Power XPDU Series Basic Power PDU with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of PDU + (8) 5-15R output receptacles on rear of PDU; UL60950-1/cUL/FCC Approved; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 3.5 lbs | 138
90000045 | XPD1420HV | Xtreme Power XPDU Series Basic Power PDU with 12' Input line cord with L5-20P plug (L5-20 to 5-20 adapter included); (6) 5-20R output receptacles on front of PDU + (8) 5-20R output receptacles on rear of PDU; UL60950-1/cUL/FCC Approved; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 4.8 lbs | 190
90000046 | XPD2420V60 | Xtreme Power XPDU Series Basic Power PDU with 12' Input line cord with L5-20P plug (L5-20 to 5-20 adapter included); (24) 5-20R output receptacles; vertical mounting only; UL60950-1/cUL/FCC Approved; 3-Year Warranty; 60"W x 1.5"D x 1.5"H, 5.6 lbs * | 182
90000053 | XPDU-IEC | Xtreme Power XPDU Series Basic Power 230V PDU with C20 inlet (power cord ordered separately), (10) IEC C13 + (2) IEC C19 output receptacles; 1U Rackmount configuration; CE Listed; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 2.6 lbs | 190
Basic PDU - 30A & 50A Models
Part Number | Model | Description | List Price
90000374 | XPD24C13V | Xtreme Power XPDU Series Basic Power PDU, 30A, 200-240V; L6-30P 6ft line cord, (24) C13 output receptacles. Vertical Mount. 1.75"W x 1.75"D x 66"L. 12 lbs | 340
90000251 | XPD31 | Xtreme Power XPDU Series Basic Power PDU, 30A, 200-240V; L6-30P 6ft line cord, (2) L6-30R, (2) L6-20R and (4) 6-15/20R output receptacles. Rackmount. 19"W x 4.7"D x 3.5"H. 9 lbs | 580
90000252 | XPD32 | Xtreme Power XPDU Series Basic Power PDU, 30A, 200-240V; L6-30P 6ft line cord, (2) L6-30R, (4) L6-20R output receptacles. Rackmount. 19"W x 2.4"D x 3.5"H. 7.5 lbs | 580
90000253 | XPD33 | Xtreme Power XPDU Series Basic Power PDU, 30A, 200-240V; L6-30P 6ft line cord, (4) IEC-C19 and (8) IEC C13 output receptacle. s Rackmount. 19"W x 2.4"D x 3.5"H. 8 lbs | 450
90000254 | XPD34 | Xtreme Power XPDU Series Basic Power PDU, 30A, 240/120V; L14-30P 6ft line cord, (2) L6-30R, (4) L6-20R and (12) 5-20R output receptacles. Rackmount. 19"W x 4.7"D x 3.5"H. 9.5 lbs | 690
90000255 | XPD35 | Xtreme Power XPDU Series Basic Power PDU, 50A, 200-240V; Hardwire input with Pigtail, (2) L6-30R and (4) L6-20R output receptacles. Rackmount. 19"W x 2.4"D x 3.5"H. 7 lbs | 580
90000256 | XPD36 | Xtreme Power XPDU Series Basic Power PDU, 50A, 200-240V; Hardwired input with Pigtail, (4) IEC-C19 and (8) IEC C13 output receptacles. Rackmount. 19"W x 2.4"D x 3.5"H. 6.8 lbs | 460
90000257 | XPD37 | Xtreme Power XPDU Series Basic Power PDU, 50A, 240/120V; Hardwired input with Pigtail, (2) L6-30R, (4) L6-20R and (12) 5-20R output receptacles. Rackmount. 19"W x 4.7"D x 3.5"H. 10 lbs | 690
90001037 | XPD38 | Xtreme Power XPDU Series Basic Power PDU, 30A, 120V; L14-30P, 6' input cord , (4) L5-30R, (4) L5-20R output receptacles. Rackmount. 19"W x 4.7"D x 3.5"H. 9.5 lbs | 690
90001038 | XPD39 | Xtreme Power XPDU Series Basic Power PDU, 50A, 120V; hardwire input with pigtail, (4) L5-30R, (4) L5-20R output receptacles. Rackmount. 19"W x 4.7"D x 3.5"H. 9.5 lbs | 690
Surge PDU
Part Number | Model | Description | List Price
90000048 | XPDS1015HV | Xtreme Power XPDU Series Surge Power PDU with 12' Input line cord with5-15P plug; (2) 5-15R surge protected output receptacles on front of PDU + (8) 5-15R surge protected output receptacles on rear of PDU; 342 Joule Rating; UL60950-1/cUL/FCC Approved; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 4.4 lbs * | 159
90000049 | XPDS1020HV | Xtreme Power XPDU Series Surge Power PDU with 12' Input line cord with L5-20P plug (L5-20 to 5-20 adapter included); (2) 5-15/20R surge protected output receptacles on front of PDU + (8) 5-15/20R surge protected output receptacles on rear of PDU; 342 Joule Rating; UL60950-1/cUL/FCC Approved; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 4.6 lbs * | 179
Value PDU
Part Number | Model | Description | List Price
90000051 | XPD1215HVPL | Xtreme Power XPDU Series Value Power PDU with 6' Input line cord with 5-15P plug; (12) 5-15R output receptacles; Plastic case; UL60950-1/cUL/FCC Approved; 3-Year Warranty; 19.0"W x 1.5"D x 1.75"H, 1.4 lbs * | 58
XBDM SERIES
Part Number | Model | Description | List Price
90000090 | XBDM-1015LV | Xtreme Power XBDM Series 15 Amp Maintenance Bypass Distribution Module with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of BDM + (4) 5-15R output receptacles on rear of BDM; bypass switch allows for maintenance of the UPS without affecting the load connected; 3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 379
90000091 | XBDM-1020LV | Xtreme Power XBDM Series20 Amp Maintenance Bypass Distribution Module with 12' Input line cord with 5-20P plug; (6) 5-20R output receptacles on front of BDM + (4) 5-20R output receptacles on rear of BDM; bypass switch allows for maintenance of the UPS without affecting the load connected; 3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 419
90000093 | XBDM-1030LV | Xtreme Power XBDM Series30 Amp Maintenance Bypass Distribution Module with 6' Input line cord with L5-30P plug; (5) 5-20R output receptacles on front of BDM (Load Group 1) + (5) 5-20R output receptacles on rear of BDM (Load Group 2); (2) bypass switches allow for maintenance of the UPS without affecting the loads connected; 3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 659
90000095 | XBDM1020HV1 | Xtreme Power XBDM Series Maintenance Bypass Distribution Module with C20 inlet for customer supplied power cord; rated at 16A; (2) IEC C19 and (4) IEC C13 output receptacles on front + (4) IEC C13 output receptacles on back; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads; Includes IEC C20 to C13 cord kit for connecting the XBDM to a T90i-1500, NXRTi-1000 or G90-1000 UPS; 3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 369
90000094 | XBDM1020HV2 | Xtreme Power XBDM Series Maintenance Bypass Distribution Module with C20 inlet for customer supplied power cord; rated at 16A; (2) IEC C19 and (4) IEC C13 output receptacles on front + (4) IEC C13 output receptacles on back; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads; Includes (2) IEC C20 to C19 cord kits for connecting the XBDM to the P90G-3000 or P90LG-3000 UPS; 3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 419
90000949 | XBDM-15RHW | Xtreme Power XBDM Series 15 Amp Maintenance Bypass Distribution Module with HW terminal block input; output is HW terminal block and (6) 5-15/20R receptacles; Cnnection to UPS is 5-15P (3ft) and 5-20R; Rackmountable; Allows fo rbypassing and maintenance of the UPS without affecting the loads connected; 3-Year Warranty (USA only); 17"W x 3.5"D x 1.75"H, 3.6 lbs | 369
90000950 | XBDM-20RHW | Xtreme Power XBDM Series 20 Amp Maintenance Bypass Distribution Module with HW terminal block input; output is HW terminal block and (6) 5-15/20R receptacles; Connection to UPS is 5-20P (3ft) and 5-20R; Rackmountable; Allows fo rbypassing and maintenance of the UPS without affecting the loads connected; 3-Year Warranty (USA only); 17"W x 3.5"D x 1.75"H, 3.6 lbs | 369
90000947 | XBDM-HW30 | Xtreme Power XBDM Series 30 Amp Maintenance Bypass Distribution Module; Hardwired input and output terminal block connection; Connection to UPS is via L5-30R receptacle and 3' power cord with L5-30P plug; Rackmountable; Includes rotary bypass switch, allowing for bypass and maintenance of the UPS without affecting the connected loads; 3-Year Warranty (USA only); 17.25"W x 5.25"D x 3.5"H, 7.3 lbs | 620
90000934 | XBDM-HW63 | Xtreme Power XBDM Series 208VAC, 63 Amp Maintenance Bypass Distribution Module; Hardwire or optional cable kit input, Hardwire terminal block output; Connects to UPS via Hardwire or optional cable kit; Make-Before-Break; includes an inverter interlock; Rackmountable; Allows for maintenance of the UPS without affecting the loads connected; Interconnect cables supplied by others; 3-Year Warranty (USA only); 17.25"W x 5.25"D x 3.5"H, 7.1 lbs | 570
Replacement Batteries and Battery Packs
Individual Replacement Batteries
Part Number | Model Number | Description | List Price
| HRL1234WF2 | 12V, 9AH Rechargeable sealed Lead Acid AGM Maintenance Free replacement battery. _____ UPS requires (_) batteries. F2 (.25 inch) faston tabs. One Year Warranty. 2.6"W x 5.9"L x 3.9"H. 6 lbs. | 59
| UPS12580 | 12V, 580Watt Rechargeable sealed Lead Acid AGM Maintenance Free replacement battery. _____ UPS requires (_) batteries. F2 (.25 inch) faston tabs. One Year Warranty. 2.6"W x 5.9"L x 9.9"H. 5 lbs. | 65
Replacement Battery Packs
Part Number | Model Number | Description | List Price
90000549 | J60-BAT1 | Replacement battery pack for J60-350 UPS (1) Required per UPS. Includes LiFePo4 batteries and Protection Circuit Module (PCM). One Year Warranty. 2.6"W x 5.0"L x 1.0"H. | 195
90001046 | J60-BAT2 | Replacement battery pack for J60-600 UPS (1) Required per UPS. Includes LiFePo4 batteries and Protection Circuit Module (PCM). One Year Warranty. 2.6"W x 5.0"L x 1.0"H. | 432
90000478 | P80-BAT580 | Replacement battery pack for P80g-5000 UPS, and P80-BP72X. (1) Required per UPS and (2) Required per BP.. One Year Warranty. 8.5"W x 18.5"L x 2.6"H. 37 lbs | 495
90000370 | P90-BAT1 | Replacement battery pack for P90-1000, P80-800 and P80-1100 UPS. (1) Required per UPS. One Year Warranty. 6.5"W x 8.0"L x 2.6"H. 13 lbs. | 245
90000371 | P90-BAT2 | Replacement battery pack for P90-1500 UPS or P90-BP36. (1) Required per UPS, (2) required per P90-BP36. One Year Warranty. 8.5"W x 12.6"L x 2.6"H. 19 lbs. | 295
90000372 | P90-BAT3 | Replacement battery pack for P90-2000, P80-1500, P80-2000 UPS or P90-BP48. (1) Required per UPS, (2) required per P90-BP48. One Year Warranty. 8.5"W x 12.6"L x 2.6"H. 25 lbs. | 350
90000373 | P90-BAT4 | Replacement battery pack for P90-3000, P90G-3000, P80-2200, P80-3000, P80G-3000 UPS or P90-BP72. (1) Required per UPS, (2) required per B90-BP72. One Year Warranty. 8.5"W x 18.5"L x 2.6"H. 37 lbs. | 465

## J60
|  | Return to Index | 2024-08-01
J60 Series Standby UPS
Part Number | MODEL | DESCRIPTION | LIST PRICE
90000465 | J60-350 | Xtreme Power J60 Series 350VA/200W Standby UPS; 120VAC; C14 inlet with C13 to 5-15P (3ft) detachable power cord; (3) 5-15R output receptacles; Lithium battery for longer life and up to 104 F operation without battery degradation; Battery Management System (BMS) insures cell voltage balancing, parallel current sharing, and overcharge/discharge protection; surge protection; Wall or Desk Mounting; UL, cUL, RoHS and TAA compliant; 5-Year Full Warranty (USA and Canada), 3-Year Full Warranty (worldwide); 6.9"W x 8.5"D x 1.25"H, 3.4 lbs | 439
90000776 | J60-600 | Xtreme Power J60 Series 600VA/360W Standby UPS; 120VAC; C14 inlet with C13 to 5-15P (3ft) detachable power cord; (3) 5-15R output receptacles; Lithium battery for longer life and up to 104 F operation without battery degradation; redundant Battery Management System (BMS) insures cell voltage balancing, parallel current sharing, and overcharge/discharge protection; surge protection; Wall or Desk Mounting; UL, cUL, RoHS and TAA compliant; 5-Year Full Warranty (USA and Canada), 3-Year Full Warranty (worldwide); 7.3"W x 10.8"D x 1.6"H, 4.7 lbs | 749
90000472 | J60i-350 | Xtreme Power J60i Series 350VA/200W Standby UPS; 230VAC; C14 inlet; (2) IEC C13 output receptacles; Lithium battery for longer life and up to 104 F operation without battery degradation; Battery Management System (BMS) insures cell voltage balancing, parallel current sharing, and overcharge/discharge protection; surge protection; Wall or Desk Mounting; CE, RoHS and TAA compliant; 5-Year Full Warranty (USA and Canada), 3-Year Full Warranty (worldwide); 6.9"W x 8.5"D x 1.25"H, 3.4 lbs | 439
90000777 | J60i-600 | Xtreme Power J60i Series 600VA/360W Standby UPS; 230VAC; C14 inlet; (2) IEC C13 output receptacles; Lithium battery for longer life and up to 104 F operation without battery degradation; redundant Battery Management System (BMS) insures cell voltage balancing, parallel current sharing, and overcharge/discharge protection; surge protection; Wall or Desk Mounting; CE, RoHS and TAA compliant; 5-Year Full Warranty (USA and Canada), 3-Year Full Warranty (worldwide); 7.3"W x 10.8"D x 1.6"H, 4.7 lbs | 749
90001061 | J60C-600 | Xtreme Power J60C Series 600VA/360W Lithium Ion UPS; 1U; 120VAC; detachable 6' input line cord with 5-15P; (5) 5-15R output receptacles, (4 battery backup, 1 surge only); Full Load Runtime = 6 min; up to 98% efficiency; Tower, Wall, or Rack mounting; Smart LCD display; Intelligent slot; USB port; UL, cTUVus, RoHSCE, RoHS, FCC , TAA Compliant; 5-Year Full Warranty (USA and Canada), 3-Year Full Warranty (worldwide); 17.2" x 8.5" x 1.7"; 7.8 lbs | 835
90001062 | J60Ci-600 | Xtreme Power J60Ci Series 600VA/360W Lithium Ion UPS; 1U; 230VAC; IEC C14 Inlet; (5) C13 output receptacles, (4 battery backup, 1 surge only); Full Load Runtime = 6 min; up to 98% efficiency; Tower, Wall, or Rack mounting; Smart LCD display; Intelligent slot; USB port; CE, RoHS, TAA Compliant; 5-Year Full Warranty (USA and Canada), 3-Year Full Warranty (worldwide); 17.2" x 8.5" x 1.7"; 7.8 lbs | 835
900007742 | JX-200 | J60 200W Isolation Transformer, 120 VAC, 50/60Hz, C14 inlet with removeable 5-15P line cord; (3) 5-15R output receptacles; 5A output breaker; complete line isolation; Common Mode and Normal Mode noise filtering; 300 joules surge suppression; UL16950, RoHS; 5-Year Full Warranty; 6.9" W x 8.5" D x 1.25" H; 6.6 lbs. | 220
90000741 | SNMP-2PV3 | Internal SNMP/WEB Card for use with J60C and J60Ci Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-EMPV2 Environmental Monitor; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 359
90000674 | SNMP-EMPV2 | Environmental Monitoring Sensor to monitor room temperature and humidity - used with SNMP-2PV3 SNMP/WEB Card. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 230
90000778 | SNMP-J60 | External SNMP/Web Card for use with J60-600(i) Series UPS; monitor critical UPS parameters, alarms, and status; output power control to reboot loads; packaging = 7.5"W x 6"D x 2.5"H, 1 lb | 279
90000785 | EMD-J60 | Environmental Monitoring Sensor to monitor ambient temperature and humidity. Include two user defined contact closures. Must be used with SNMP-J60 External SNMP Card. Packaging = 5.7"W x 5.2"D x 1.7"H, 1 lb | 195
N/A | XPC-515P-3RA | Optional 3ft, 5-15P line cord with right angle offset for use with J60-350. Weight: .5 lbs | 22
N/A | XPC-515P-6RA | Optional 6ft, 5-15P line cord with right angle offset for use with J60-350. Weight: .5 lbs | 22
90000090 | XBDM-1015LV | Xtreme Power XBDM Series 15 Amp Maintenance Bypass Distribution Module with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of BDM + (4) 5-15R output receptacles on rear of BDM; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads;3-Year Warranty (USA and Canada); 19"W x 3.5"D x 1.75"H, 3.5 lbs For use with 700VA, 1000VA, 1500VA V80 Series | 379
90000041 | XPD1415HV | Xtreme Power XPDU Series Basic Power PDU with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of PDU + (8) 5-15R output receptacles on rear of PDU; UL60950-1/cUL/FCC Approved; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 3.5 lbs | 138
90000765 | J60-DIN | DIN Rail mount for J60 | 19

## A60
|  | Return to Index | 2024-08-01
A60 - Standby UPS
Part Number | MODEL | DESCRIPTION | LIST PRICE
90000875 | A60-550 | Xtreme Power A60 Series 550VA/330W Standby UPS 120VAC; 6' Input line cord with 5-15P plug; (10) 5-15R output receptacles, (5 battery backup + 5 surge only); Tower, Desk or Wall Mounting; USB Port, Communication Cable and Shutdown Software; UL, cUL, RoHS approved, TAA Compliant; 3 Year Full Warranty (USA and Canada only); $25K Load Protection Policy; 6.2"W x 12"D x 3.7"H, 5.7 lbs | 125
90000876 | A60-850 | Xtreme Power A60 Series 850VA/500W Standby UPS 120VAC; 6' Input line cord with 5-15P plug; (10) 5-15R output receptacles, (5 battery backup + 5 surge only); Tower, Desk or Wall Mounting; touch screen display; USB Charging Port; USB Communication Port, Communication Cable and Shutdown Software; UL, cUL, RoHS approved, TAA Compliant; 3 Year Full Warranty (USA and Canada only); $25K Load Protection Policy; 6.2"W x 12"D x 3.7"H, 6.4 lbs | 165
90000281 | SNMP-USB | External SNMP/Web Card for use with A60 Series UPS; packaging = 7.5"W x 6"D x 2.5"H, 2lbs | 325
90001033 | A605SP | Xtended 5YR Factory Warranty for A60 Series UPS (USA Only) - 5 Year Coverage includes coverge of electronics and batteries, telephone technical support, advanced exchange and ground shipment both ways. | 69

## S71
|  | Return to Index | 2024-08-01
S71 Line Interactive UPS
Part Number | MODEL | DESCRIPTION | LIST PRICE
90001237 | S71-700 | XPC S71 Series 700VA/420W Line-Interactive Tower UPS 120VAC; 6' detachable Input line cord with 5-15P plug; (4) 5-15R output receptacles; touch LCD display; 465 Joule surge suppression rating; Auto Restart; USB Port, Communications Cable and Shutdown Software; UL/cUL listed, RoHS, TAA Compliant; 3-Year Full Warranty (USA and Canada); $25K Load Protection Policy; 3.9"W x 11.3"D x 5.6"H, 11.2 lbs | 189
90001238 | S71-1000 | XPC S71 Series 1000VA/600W Line-Interactive Tower UPS 120VAC; 6' Input line cord with 5-15P plug; (6) 5-15R output receptacles; touch LCD display; 465 Joule surge suppression rating; Auto Restart; USB Port, Communications Cable and Shutdown Software; RJ45 Surge protection port; UL/cUL listed, RoHS, TAA Compliant; 3-Year Full Warranty (USA and Canada); $25K Load Protection Policy; 5.1"W x 12.6"D x 5.6"H, 18.0 lbs | 275
90001240 | S71-1500 | XPC S71 Series 1500VA/900W Line-Interactive Tower UPS 120VAC; 6' Input line cord with 5-15P plug; (6) 5-15R output receptacles; touch LCD display; 465 Joule surge suppression rating; Auto Restart; USB Port, Communications Cable and Shutdown Software; RJ45 Surge protection port; UL/cUL listed, RoHS, TAA Compliant; 3-Year Full Warranty (USA and Canada); $25K Load Protection Policy; 5.1"W x 12.6"D x 7.1"H, 23.0 lbs | 389
90000281 | SNMP-USB | External SNMP/Web Card for use with XST or S70 Series UPS; packaging = 7.5"W x 6"D x 2.5"H, 2 lbs | 325
90000248 | S715SP57 | Xtended 5YR Factory Warranty for S71-700 (USA and Canada) - 5 Year Coverage includes coverage of electronics and batteries, telephone technical support, advanced exchange and ground shipping both ways. | 95
90000249 | S715SP152 | Xtended 5YR Factory Warranty for S71-1000/1500 (USA and Canada) - 5 Year Coverage includes coverage of electronics and batteries, telephone technical support, advanced exchange and ground shipping both ways.. | 140

## V80
|  | Return to Index | 2024-08-01
V80 Series Line Interactive UPS LA Batteries
Part Number | MODEL | DESCRIPTION | LIST PRICE
90000853 | V80-700 | Xtreme Power V80 Series 700VA/420W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable batteries; 1-6A adjustable charger; Full Load Runtime = 2.3 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 24 lbs | 499
90000890 | V80-700XR1 | Xtreme Power V80 Series 700VA/420W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable batteries; 1-6A adjustable charger; Full Load Runtime = 4.3 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 25.5 lbs | 565
90000891 | V80-700XR2 | Xtreme Power V80 Series 700VA/420W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable batteries; 1-6A adjustable charger; Full Load Runtime = 13 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 31 lbs | 625
90000892 | V80-700XR3 | Xtreme Power V80 Series 700VA/420W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable batteries; 1-6A adjustable charger; Full Load Runtime = 21 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 37 lbs | 685
90000893 | V80-700XR4 | Xtreme Power V80 Series 700VA/420W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable batteries; 1-6A adjustable charger; Full Load Runtime = 22 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 43 lbs | 745
90000854 | V80-1000 | Xtreme Power V80 Series 1000VA/600W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable batteries; 1-6A adjustable charger; Full Load Runtime = 2.7 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 27.3 lbs | 659
90000894 | V80-1000XR1 | Xtreme Power V80 Series 1000VA/600W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable batteries; 1-6A adjustable charger; Full Load Runtime = 6.0 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 31.3 lbs | 755
90000895 | V80-1000XR2 | Xtreme Power V80 Series 1000VA/600W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable batteries; 1-6A adjustable charger; Full Load Runtime = 16.0 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 43 lbs | 865
90000855 | V80-1500 | Xtreme Power V80 Series 1500VA/900W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable batteries; 1-6A adjustable charger; Full Load Runtime = 1.6 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 29.3 lbs | 749
90000896 | V80-1500XR1 | Xtreme Power V80 Series 1500VA/900W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable batteries; 1-6A adjustable charger; Full Load Runtime = 3.8 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 32.3 lbs | 809
90000897 | V80-1500XR2 | Xtreme Power V80 Series 1500VA/900W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable batteries; 1-6A adjustable charger; Full Load Runtime = 11 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 32.3 lbs | 949
90000856 | V80-2000 | Xtreme Power V80 Series 2000VA/1200W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C19 to 5-20 input line cord; (8) 5-15R output receptacles ; Hot Swappable batteries; 1-6A adjustable charger; Full Load Runtime = 1.6 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 31.3 lbs | 869
90000898 | V80-2000XR1 | Xtreme Power V80 Series 2000VA/1200W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C19 to 5-20 input line cord; (8) 5-15R output receptacles ; Hot Swappable batteries; 1-6A adjustable charger; Full Load Runtime = 1.7 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 34.3 lbs | 899
90000899 | V80-2000XR2 | Xtreme Power V80 Series 2000VA/1200W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C19 to 5-20 input line cord; (8) 5-15R output receptacles ; Hot Swappable batteries; 1-6A adjustable charger; Full Load Runtime = 4.4 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 46.3 lbs | 1039
V80 Lithium 700-1500 SERIES - 120 Volt with Lithium Batteries
Part Number | MODEL | DESCRIPTION | LIST PRICE
90000857 | V80-0.7kLi1 | Xtreme Power V80 Series 700VA/420W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable LiFeP04 batteries; 1-6A adjustable charger; Full Load Runtime = < 3 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 5 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 21.2 lbs | 999
90000967 | V80-0.7kLi2 | Xtreme Power V80 Series 700VA/420W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable LiFeP04 batteries; 1-6A adjustable charger; Full Load Runtime = 16 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 5 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 23.4 lbs | 1399
90000968 | V80-0.7kLi3 | Xtreme Power V80 Series 700VA/420W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable LiFeP04 batteries; 1-6A adjustable charger; Full Load Runtime = 18 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 5 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 25.6 lbs | 1799
90000969 | V80-0.7kLi4 | Xtreme Power V80 Series 700VA/420W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable LiFeP04 batteries; 1-6A adjustable charger; Full Load Runtime = 22 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 5 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 27.8 lbs | 2199
90000858 | V80-1kLi1 | Xtreme Power V80 Series 1000VA/600W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable LiFeP04 batteries; 1-6A adjustable charger; Full Load Runtime = 7 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 5 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 24.2 lbs | 1549
90000970 | V80-1kLi2 | Xtreme Power V80 Series 1000VA/600W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable LiFeP04 batteries; 1-6A adjustable charger; Full Load Runtime = 20 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 5 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 28.6 lbs | 2349
90000859 | V80-1.5kLi1 | Xtreme Power V80 Series 1500VA/900W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable LiFeP04 batteries; 1-6A adjustable charger; Full Load Runtime = <3 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 5 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 26 lbs | 1639
90000971 | V80-1.5kLi2 | Xtreme Power V80 Series 1500VA/900W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable LiFeP04 batteries; 1-6A adjustable charger; Full Load Runtime = 11 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 5 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 30.4 lbs | 2439
V80HT Series 700-2000 - 120 Volt with Lead Acid High Temperature Batteries
Part Number | MODEL | DESCRIPTION | LIST PRICE
90000864 | V80-700HT1 | Xtreme Power V80 Series 700VA/420W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable High Temperature Batteries; 1-6A adjustable charger; Full Load Runtime = 3.6 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 25.5 lbs | 579
90000861 | V80-700HT2 | Xtreme Power V80 Series 700VA/420W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable High Temperature Batteries; 1-6A adjustable charger; Full Load Runtime = 10 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 31 lbs | 689
90000862 | V80-700HT3 | Xtreme Power V80 Series 700VA/420W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable High Temperature Batteries; 1-6A adjustable charger; Full Load Runtime = 21 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 37 lbs | 799
90000863 | V80-700HT4 | Xtreme Power V80 Series 700VA/420W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable High Temperature Batteries; 1-6A adjustable charger; Full Load Runtime = 22 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 43 lbs | 909
90000865 | V80-1000HT1 | Xtreme Power V80 Series 1000VA/600W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable High Temperature Batteries; 1-6A adjustable charger; Full Load Runtime = 4.9 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 31.3 lbs | 799
90000864 | V80-1000HT2 | Xtreme Power V80 Series 1000VA/600W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable High Temperature Batteries; 1-6A adjustable charger; Full Load Runtime = 14.0 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 43 lbs | 1019
90000866 | V80-1500HT1 | Xtreme Power V80 Series 1500VA/900W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable High Temperature Batteries; 1-6A adjustable charger; Full Load Runtime = 3.2 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 32.3 lbs | 879
90000865 | V80-1500HT2 | Xtreme Power V80 Series 1500VA/900W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C13 to 5-15 input line cord; (8) 5-15R output receptacles ; Hot Swappable High Temperature Batteries; 1-6A adjustable charger; Full Load Runtime = 9 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 32.3 lbs | 1099
90000867 | V80-2000HT1 | Xtreme Power V80 Series 2000VA/1200W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C19 to 5-20 input line cord; (8) 5-15R output receptacles ; Hot Swappable High Temperature Batteries; 1-6A adjustable charger; Full Load Runtime = 1.7 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 34.3 lbs | 999
90000966 | V80-2000HT2 | Xtreme Power V80 Series 2000VA/1200W; Line-Interactive UPS; 2U; 120VAC; pure sinewave output; 5' detachable C19 to 5-20 input line cord; (8) 5-15R output receptacles ; Hot Swappable High Temperature Batteries; 1-6A adjustable charger; Full Load Runtime = 4.4 min; ECO mode; Tower and rack mounting; Smart LCD screen; Intelligent slot; RS-232, USB port, and EPO connections; UL, cUL, RoHS approved; TAA Compliant 3 year full Warranty (USA and Canada); 25K load protection policy; 17.2" x 16.1" x 3.5"; 46.3 lbs | 1219
V80 Series Accessories
Part Number | MODEL | DESCRIPTION | LIST PRICE
90000741 | SNMP-2PV3 | Internal SNMP/WEB Card for use with V80, P80 or P91(g) Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-EMPV2 Environmental Monitor; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 359
90000674 | SNMP-EMPV2 | Environmental Monitoring Sensor to monitor room temperature and humidity - used with SNMP-2PV3 SNMP/WEB Card. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 230
90000265 | RELAY-MINI | Dry Contact RELAY CARD with DB9 & terminal block adapter; packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 120
90000406 | XPC-2PRAIL | 2-Post Rail Kit for V80, P80, P91(g) and NXRT 800VA thru 5kVA UPS or EBM; rated for 125 lbs; 4"W x 20"D x 3"H. 5 lbs. | 102
90000116 | XPC-2POSTL | 2-Post Shelf Kit for V80, P91(g)-1000, 1500, 2000, 3000; rated for 150lbs; 21.5"W x 23.3"D x 3.5"H. 9 lbs. | 160
90000392 | PV-WMB | Wall mount bracket for use with V80, P80, P91(g) and P91L series UPSs and battery packs up to 5KVA; 4"W x 24"D x 4"H. 5 lbs. | 80
90000090 | XBDM-1015LV | Xtreme Power XBDM Series 15 Amp Maintenance Bypass Distribution Module with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of BDM + (4) 5-15R output receptacles on rear of BDM; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads;3-Year Warranty (USA and Canada); 19"W x 3.5"D x 1.75"H, 3.5 lbs For use with 700VA, 1000VA, 1500VA V80 Series | 379
90000409 | V805SP71 | Xtended 5YR Factory Warranty for V80-700 and V80-1000 (USA and Canada) - 5 Year Coverage includes coverage of electronics and internal batteries, telephone technical support, advanced exchange and ground shipping both ways. | 225
90000410 | V805S52 | Xtended 5YR Factory Warranty for V80-1500 and V80-2000 (USA and Canada) - 5 Year Coverage includes coverage of electronics and internal batteries, telephone technical support, advanced exchange and ground shipping both ways. | 360
90000409 | V80HT5SP71 | Xtended 5YR Factory Warranty for V80-700 and V80-1000 (USA and Canada) - 5 Year Coverage includes coverage of electronics and internal batteries, telephone technical support, advanced exchange and ground shipping both ways. | 225
90000410 | V80HT5SP52 | Xtended 5YR Factory Warranty for V80HT-1500 and V80HT-2000 (USA and Canada) - 5 Year Coverage includes coverage of electronics and internal batteries, telephone technical support, advanced exchange and ground shipping both ways. | 360

## P80
|  | Return to Index | 2024-08-01
P80 Series Line Interactive UPS
Part Number | MODEL | DESCRIPTION | LIST PRICE
90000900 | P80-800 | Xtreme Power P80 Series 800VA/720W; Line-Interactive UPS; true Sinewave output; 2U; 120VAC; 1.5A charger; Full Load Runtime = 4 min; 6' input line cord with 5-15 plug; (8) 5-15R output receptacles; Tower and rack mounting; 97% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; UL, cUL, RoHS approved; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 15.1"D x 3.5"H; 29 lbs | 789
90000901 | P80-1100 | Xtreme Power P80 Series 1100VA/990W; Line-Interactive UPS; true Sinewave output; 2U; 120VAC; 1.5A charger; Full Load Runtime = 3 min; 6' input line cord with 5-15 plug; (8) 5-15R output receptacles; Tower and rack mounting; 97% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; UL, cUL, RoHS approved; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 15.1"D x 3.5"H; 30 lbs | 849
90000902 | P80-1500 | Xtreme Power P80 Series 1500VA/1350W; Line-Interactive UPS; true Sinewave output; 2U; 120VAC; 1.5A charger; Full Load Runtime = 4 min; 6' input line cord with 5-15 plug; (8) 5-15R output receptacles; Tower and rack mounting; 97% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; UL, cUL, RoHS approved; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 18.9"D x 3.5"H; 43 lbs | 1099
90000955 | P80-2000 | Xtreme Power P80 Series 2000VA/1800W; Line-Interactive UPS; true Sinewave output; 2U; 120VAC; 1.5A charger; Full Load Runtime = 4 min; 6' input line cord with 5-20 plug; (8) 5-15/20R output receptacles; Tower and rack mounting; 97% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; UL, cUL, RoHS approved; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 18.9"D x 3.5"H; 48 lbs | 1249
90000903 | P80-2200 | Xtreme Power P80 Series 2200VA/2000W; Line-Interactive UPS; true Sinewave output; 2U; 120VAC; 1.5A charger; Full Load Runtime = 4 min; 6' input line cord with 5-20 plug; (8) 5-15/20R output receptacles; Tower and rack mounting; 97% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; UL, cUL, RoHS approved; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 23.6"D x 3.5"H; 68 lbs | 1569
90000904 | P80-3000 | Xtreme Power P80 Series 3000VA/2700W; Line-Interactive UPS; true Sinewave output; 2U; 120VAC; 1.5A charger; Full Load Runtime = 4 min; 6' input line cord with L5-30 plug; (8) 5-15/20R output receptacles; Tower and rack mounting; 97% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; UL, cUL, RoHS approved; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 23.6"D x 3.5"H; 71 lbs | 1729
90000529 | P80-3000V2 | Xtreme Power P80 Series 3000VA/2700W; Line-Interactive UPS; true Sinewave output; 2U; 120VAC; 1.5A charger; Full Load Runtime = 4 min; 6' input line cord with L5-30 plug; (6) 5-15/20R and (1) L5-30R output receptacles; Tower and rack mounting; 97% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; UL, cUL, RoHS approved; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 23.6"D x 3.5"H; 71 lbs | 1729
90000954 | P80g-3000 | Xtreme Power P80g Series 3000VA/2700W; Line-Interactive UPS; true sinewave output; 2U; 208-240VAC; 1.5A charger; Full Load Runtime = 4 min; IEC C19 to L6-20P detachable input line cord (8 ft); (1) IEC C19 + (8) IEC C13 output receptacles; Tower and rack mounting; 99% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; CE and RoHS approved; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 23.6"D x 3.5"H. 71 lbs | 1670
Bundle | P80g-3KTB | Xtreme Power P80g Series 3000VA/2700W UPS and XPD-IT15A Bundle; Line-Interactive, true sinewave UPS with 1500VA/1500W 120V Transformer PDU; 208VAC input -208/120V output; Full Load Runtime = 4 min; System has IEC-C19 to L6-20P detachable input line cord (8 ft); Output receptacles include (1) IEC C19 + (7) IEC C13 (208V) + (16) 5-15R (120V). Rack mounting; 99% efficiency in ECO mode; 1.5A charger; UPS and PDU LCD screens; RS-232 and USB port connections; 3 year full Warranty (USA and Canada); 50K load protection policy; UPS 17.2"W x 23.6"D x 3.5"H. 71 lbs. Transformer 17.5"W x 15"D x 3.5"H , 43 lbs Package Includes: P80g-3000 UPS Power Module (2U) XPD-IT15A Transformer Module (2U) UPS to Transformer Cable C13 to C14 Software P90-Rail 4-Post Rail Kit | 2920
90000430 | P80g-5000 | Xtreme Power P80g Series 5000VA/4500W; Line-Interactive UPS; true sinewave output; 2U; 208-240VAC; 1.5A charger; Full Load Runtime = 2.5 min; L6-30P input line cord (6 ft); (1) L6-30R + (4) IEC C19 output receptacles; Tower and rack mounting; 99% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; CE and RoHS approved; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 23.6"D x 3.5"H. 85 lbs | 2750
Bundle | P80g-5KB1 | Xtreme Power P80g Series 5000VA/4500W; Line-Interactive UPS; true sinewave output; 2U; 208-240VAC; 1.5A charger; Full Load Runtime = 2.5 min; L6-30P input line cord (6 ft); (2) L6-30R + (2) L6-20R + (1) IEC C19 output receptacles; Tower and rack mounting; 99% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; CE and RoHS approved; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 23.6"D x 3.5"H. 90 lbs | 2987
Bundle | P80g-5KB2 | Xtreme Power P80g Series 5000VA/4500W; Line-Interactive UPS and XPD24C13V PDU bundle; true sinewave output; 2U; 208-240VAC; 1.5A charger; Full Load Runtime = 2.5 min; L6-30P input line cord (6 ft); (4) IEC C19 + (24) IEC C13 output receptacles; Tower and rack mounting; 99% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; CE and RoHS approved; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 23.6"D x 3.5"H. 97 lbs | 3090
Bundle | P80g-5KTB | Xtreme Power P80g Series 5000VA/4500W; Line-Interactive UPS and XPD-IT60A Transformer PDU bundle; true sinewave output; 2U; 208V or 240V in, 208/104V or 240/120V out, Max. 120V load is 4KW; 1.5A charger; Full Load Runtime = 2.5 min; L6-30P input line cord (6 ft); (2) L6-30R, (2) L6-20R and (12) 5-15/20R output receptacles; Tower and rack mounting; 99% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; CE and RoHS approved; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 23.6"D x 7"H (4U). 147 lbs. Bundle includes: P80G-5000 UPS, IT60A transformer PDU, (3) receptacle dongles, (2) 4-post rail kits. | 5427
90000916 | P90-BP48 | Extended Runtime Battery Pack for use with P80-1500, P80-2000, P90-2000 or P90L-2000 UPSs; (includes 8 each 12V9AH batteries); __ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower or Rack Mounting; TUV/UL, RoHS, cUL Approved; 3-Year Full Warranty (USA only); 17.2"W x 18.9"D x 3.5"H; 74.6 lbs | 990
90000917 | P90-BP72 | Extended Runtime Battery Pack for use with P80-2200, P80-3000, P80g-3000, or P90/P90L-3000 and P90g/P90Lg-3000 UPSs; (includes 12 each 12V9AH batteries) ;__ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower or Rack Mounting; TUV/UL, RoHS, cUL Approved; 3-Year Full Warranty (USA only); 17.2"W x 23.6"D x 3.5"H; 104.4 lbs | 1290
90000432 | P80-BP72X | Extended Runtime Battery Pack for use with P80g-5000 UPS; (includes (12) 12V 580W at 5 min rate batteries) ;__ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower or Rack Mounting; CE, RoHS Approved; 3-Year Full Warranty (USA only); 17.2"W x 23.6"D x 3.5"H; 110.4 lbs | 1720
90000909 | P90-RAIL | 4-Post Rail Kit for use with P80-800VA thru 5KVA or P90-1KVA thru 3KVA UPS or EBM; extends from 18.75" to 30.9"; packaging 3.8"W x 19.8"D x 2.8"H. 5 lbs. | 135
90000933 | P90L-RAIL | Adjustable Mounting 4-Post Rail Kit for P91 or P90L-5K, 6K, &10K UPS, BP & Transformer Module; extends from 21" to 35.5"; packaging = 3..8"W x 22"D x 2.8"H, 5 lbs | 149
90000406 | XPC-2PRAIL | 2-Post Rail Kit for P80, P90, P90L and NXRT 800VA thru 5kVA UPS or EBM; rated for 125 lbs; 4"W x 20"D x 3"H. 5 lbs. | 102
90000116 | XPC-2POSTL | 2-Post Shelf Kit for P80-800VA thru 5kVA or P90-1KVA thru 3KVA UPS or EBM; rated for 150 lbs; 21.5"W x 23.3"D x 3.5"H. 9 lbs. | 160
90001273 | XPC-2PRLV2 | 2-Post Shelf Kit with front ears for P80(g); rated for 160lbs; 21.5"W x 23.3"D x 3.5"H. 9 lbs. | 225
90000392 | PV-WMB | Wall mount bracket for use with P80, P90 and P90L series UPSs and battery packs up to 5KVA; 4"W x 24"D x 4"H. 5 lbs. | 80
90000377 | P90-FRMB | Front Rackmount Bracket for P80 800VA through 2KVA size or P90 1KVA thru 2KVA size. Required when front mounting the UPS to a 2 post or 4 post rack with no rail kit. | 36
90000741 | SNMP-2PV3 | Internal SNMP/WEB Card for use with P80 or P90 Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-EMPV2 Environmental Monitor; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 359
90000674 | SNMP-EMPV2 | Environmental Monitoring Sensor to monitor room temperature and humidity - used with SNMP-2PV3 SNMP/WEB Card. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 230
90000267 | MODBUS-IN | MODBUS CARD for use with the P80 or P90 Series UPS. Packaging = 7.25"W x 6"D x 2.5"H, 1 lbs | 319
90000265 | RELAY-MINI | Dry Contact RELAY CARD with DB9 & terminal block adapter. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 120
90000090 | XBDM-1015LV | Xtreme Power XBDM Series 15 Amp Maintenance Bypass Distribution Module with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of BDM + (4) 5-15R output receptacles on rear of BDM; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads;3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 379
90000091 | XBDM-1020LV | Xtreme Power XBDM Series 20 Amp Maintenance Bypass Distribution Module with 12' Input line cord with 5-20P plug; (6) 5-20R output receptacles on front of BDM + (4) 5-20R output receptacles on rear of BDM; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads; 3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 419
90000093 | XBDM-1030LV | Xtreme Power XBDM Series 30 Amp Maintenance Bypass Distribution Module with 6' Input line cord with L5-30P plug; (5) 5-20R output receptacles on front of BDM (Load Group 1) + (5) 5-20R output receptacles on rear of BDM (Load Group 2); (2) bypass switches allowing for bypassing and maintenance of the UPS without affecting the connected loads; 3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 659
90000041 | XPD1415HV | Xtreme Power XPDU Series Basic Power PDU with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of PDU + (8) 5-15R output receptacles on rear of PDU; UL60950-1/cUL/FCC Approved; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 3.5 lbs | 138
90000045 | XPD1420HV | Xtreme Power XPDU Series Basic Power PDU with 12' Input line cord with L5-20P plug (L5-20 to 5-20 adapter included); (6) 5-20R output receptacles on front of PDU + (8) 5-20R output receptacles on rear of PDU; UL60950-1/cUL/FCC Approved; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 4.8 lbs | 190
TBD | XPC-ZLC20-620R | P80g/90g Output Cord, 1ft, IEC Locking C20 to 6-15/20R. 3 lbs. | 79
TBD | XPC-ZLC20-L620R | P80g/90g Output Cord,1ft, IEC Locking C20 to L6-20R. 3 lbs. | 79
TBD | XPC-ZLC20-L630R | P80g/90g Output Cord, 1ft, IEC Locking C20 to L6-30R. 3 lbs. | 79
TBD | XPC-C14-615R | P80g/90g Output Cord, 1ft, IEC C14 to 6-15R. 3 lbs. | 45
90000094 | XBDM1020HV2 | Xtreme Power XBDM Series Maintenance Bypass Distribution Module for use with P80G-3000 or P90G-3000 UPS; C20 input receptacle; rated at 16A; (2) IEC C19 and (4) IEC C13 output receptacles on front + (4) IEC C13 output receptacles on back; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads; Includes (2) IEC C20-C19 cord kit; 3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 419
90000374 | XPD24C13V | Xtreme Power XPDU Series Basic Power PDU, 30A, 200-240V; L6-30P 6ft line cord, (24) C13 output receptacles. Vertical Mount. 1.75"W x 1.75"D x 66"L. 12 lbs | 340
90000251 | XPD31 | Xtreme Power XPDU Series Basic Power PDU, 30A, 200-240V; L6-30P 6ft line cord, (2) L6-30R, (2) L6-20R and (4) 6-15/20R output receptacles. Rackmount. 19"W x 4.7"D x 3.5"H. 9 lbs | 580
90000252 | XPD32 | Xtreme Power XPDU Series Basic Power PDU, 30A, 200-240V; L6-30P 6ft line cord, (2) L6-30R, (4) L6-20R output receptacles. Rackmount. 19"W x 2.4"D x 3.5"H. 7.5 lbs | 580
90000253 | XPD33 | Xtreme Power XPDU Series Basic Power PDU, 30A, 200-240V; L6-30P 6ft line cord, (4) IEC C19 and (8) IEC C13 output receptacles. Rackmount. 19"W x 2.4"D x 3.5"H. 8 lbs | 450
90000053 | XPDU-IEC | Xtreme Power XPDU Series Basic Power 230V PDU with C20 inlet (power cord ordered separately), (10) IEC C13 + (2) IEC C19 output receptacles; 1U Rackmount configuration; CE Listed; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 2.6 lbs | 190
90000407 | XPD-IT60A | Xtreme Power XPDU Series 6KVA PDU with Isolation Transformer for use with P80G-5000 or P91 5-10K UPS. 6000W, 208 or 240 in, 208/104V or 240/120V out. 3ft L6-30P Input Cord. (1) L6-30R and (12) 5-15-20R output receptacles; rear panel 208/240 voltage selection switch; includes front panel rackmount brackets; ROHS Approved; 3-Year Warranty; 17.3"W x 18"D x 3.5"H (2U), 137 lbs. | 1750
90000269 | XAT-400 | 400VA Step Down Transformer, 208V to 120V for P80G/P90G and P90LG-3000. Input is 208V IEC C14 on 2ft cord; output is 120V 5-15R on 2ft cord. 7"W x 6.8"D x 5.9"H. 8 lbs. | 600
90000739 | XPD-IT15A | Xtreme Power XPDU Series PDU with Isolation Transformer. 1500W, 208V in, 120V out. IEC-C14 inlet with 3' 5-15 line cord ; (16) 5-15R output receptacles protected by 15A breaker; 3-Year Warranty; 17.5"W x 15"D x 3.5"H (2U), 43 lbs. | 980
90000522 | P905SP15 | Xtended 5YR Factory Warranty for P80-800/1100/1500 or P90-1000/1500VA UPS (USA only) - 5 Year Coverage includes coverage of electronics and internal batteries, telephone technical support, advanced exchange and ground shipping both ways. | 375
90000523 | P905SP23 | Xtended 5YR Factory Warranty for P80-2000/2200/3000 and P80g-3000 or P90-2000/3000VA and P90g-3000 UPS (USA only) - 5 Year Coverage includes coverage of electronics and internal batteries, telephone technical support, advanced exchange and ground shipping both ways. | 610
90000431 | P805SP5 | Xtended 5YR Factory Warranty for P80g-5000 UPS (USA only) - 5 Year Coverage includes coverage of electronics and internal batteries, telephone technical support, advanced exchange and ground shipping both ways. | 800
90000524 | P90L5SPBP | Xtended 5YR Factory Warranty for P90-BP48/BP72 (USA only) - 5 Year Coverage includes coverage of battery pack, telephone technical support, advanced exchange and ground shipping both ways. | 320

## J90
|  | Return to Index | 2025-07-18
J90(i) 1-1.5k SERIES - 120(230)volt with Lithium-ion Batteries
Part Number | MODEL | DESCRIPTION | LIST PRICE
90001298 | J90-1KLi | Xtreme Power J90 Series 1000VA/900W; Online UPS with Lithium-ion batteries; 1U; 120VAC; C14 inlet with 5' input line cord with 5-15P; (4) 5-15R individually switchable output receptacles (with optional web/SNMP card); 4 hour typical recharge; Full Load Runtime = 6.5 min; Tower , rack, or wall mounting; Smart LCD display; Intelligent slot; RS-232 and USB port; Remote On/Off connection; UL, cUL, RoHS approved; FCC Class A, UN38.3; 6-year full warranty (electronics and batteries) applies for installations where the ambient temperature remains at or below 30°C (86°F) in the USA and Canada. For environments exceeding 30°C, a 3-year warranty applies; 50K load protection policy; 17.2" x 18.8" x 1.7"; 27.3 lbs. | 2450
90001301 | J90-1.5KLi | Xtreme Power J90 Series 1500VA/1350W; Online UPS with Lithium-ion batteries; 1U; 120VAC; 6' input line cord with 5-15P; (4) 5-15R individually switchable output receptacles (with optional web/SNMP card); 4 hour typical recharge; Full Load Runtime = 7 min; Tower , rack, or wall mounting; Smart LCD display; Intelligent slot; RS-232 and USB port; Remote On/Off connection; UL, cUL, RoHS approved; FCC Class A, UN38.3; 6-year full warranty (electronics and batteries) applies for installations where the ambient temperature remains at or below 30°C (86°F) in the USA and Canada. For environments exceeding 30°C, a 3-year warranty applies; 50K load protection policy; 17.2" x 20.0" x 1.7"; 27.8 lbs. | 2730
90001299 | J90i-1KLi | Xtreme Power J90i Series 1000VA/900W; Online UPS with Lithium-ion batteries; 1U; 230VAC; C14 inlet ; (4) IEC C13 individually switchable output receptacles (with optional web/SNMP card); 4 hour typical recharge; Full Load Runtime = 6.5 min; Tower , rack, or wall mounting; Smart LCD display; Intelligent slot; RS-232 and USB port; Remote On/Off connection; CE, RoHS approved; UN38.3; 6-year full warranty (electronics and batteries) applies for installations where the ambient temperature remains at or below 30°C (86°F) in the USA and Canada. For environments exceeding 30°C, a 3-year warranty applies; 50K load protection policy; 17.2" x 18.8" x 1.7"; 26.4 lbs. | 2400
90001302 | J90i-1.5KLi | Xtreme Power J90i Series 1500VA/1350W; Online UPS with Lithium-ion batteries; 1U; 230VAC; C14 inlet ; (4) IEC C13 individually switchable output receptacles (with optional web/SNMP card); 4 hour typical recharge; Full Load Runtime = 7 min; Tower , rack, or wall mounting; Smart LCD display; Intelligent slot; RS-232 and USB port; Remote On/Off connection; CE, RoHS approved; UN38.3; 6-year full warranty (electronics and batteries) applies for installations where the ambient temperature remains at or below 30°C (86°F) in the USA and Canada. For environments exceeding 30°C, a 3-year warranty applies; 50K load protection policy; 17.2" x 20.0" x 1.7"; 27.7 lbs. | 2680
90000741 | SNMP-2PV3 | Internal SNMP/WEB Card for use with J90 or J90i Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-EMPV2 Environmental Monitor; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 359
90000674 | SNMP-EMPV2 | Environmental Monitoring Sensor to monitor room temperature and humidity - used with SNMP-2PV3 SNMP/WEB Card. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 230
90000265 | RELAY-MINI | RELAY CARD with DB9 & terminal block adapter; packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 120
90000090 | XBDM-1015LV | Xtreme Power XBDM Series 15 Amp Maintenance Bypass Distribution Module with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of BDM + (4) 5-15R output receptacles on rear of BDM; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads;3-Year Warranty (USA and Canada); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 379
90000041 | XPD1415HV | Xtreme Power XPDU Series Basic Power PDU with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of PDU + (8) 5-15R output receptacles on rear of PDU; UL60950-1/cUL/FCC Approved; 3-Year Warranty (USA and Canada); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 138
90000909 | P90-RAIL | 4-Post Rail Kit for use with P91(g)-1000, 1500, 2000, 3000; 3.8"W x 19.8"D x 2.8"H. 5 lbs. | 135
90001036 | P91ADVEX | Advanced Exchange Warranty Upgrade for advanced warranty exchange and shipping for J90(i) and P91(g) UPS (USA and Canada) | 250

## P91(g) 1-3k Lead Acid
|  | Return to Index | 2024-08-01
P91 1-3K SERIES - 120 Volt with Lead Acid Batteries
Part Number | MODEL | DESCRIPTION | LIST PRICE
90000621 | P91c-1000 | Xtreme Power P91 Series 1000VA/800W; Online UPS; 1U; 120VAC; C14 inlet with 5' C13 to 5-15P input line cord; (3) 5-15R output receptacles; Hot Swappable batteries; 1A charger; Full Load Runtime = 8 min; Front mount rack brackets included; 98% efficiency in ECO mode; Smart LED display; Intelligentt slot; USB port and REPO connections; UL, cUL, RoHS approved; FCC Class A; TAA Compliant; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2" x 17.8" x 1.7"; 28 lbs | 1130
90000756 | P91-1000 | Xtreme Power P91 Series 1000VA/1000W; Online UPS; 2U; 120VAC; 6' input line cord with 5-15 plug; (8) 5-15R output receptacles, (4) of the output receptacles programmable as group ; Hot Swappable batteries; 1-8A adjustable charger; Full Load Runtime = 3 min; Tower and rack mounting; 98% efficiency in ECO mode; Smart LCD screen; Intelligent slot; RS-232, USB port, and REPO connections; UL, cUL, RoHS approved; FCC Class B; TAA Compliant; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2" x 15.1" x 3.5"; 25.5 lbs | 1165
90000622 | P91-1500 | Xtreme Power P91 Series 1500VA/1450W; Online UPS; 2U; 120VAC; 6' input line cord with 5-15 plug; (8) 5-15R output receptacles, (4) of the output receptacles programmable as group; Hot Swappable batteries; 1-8A adjustable charger; Full Load Runtime = 3 min; Tower and rack mounting; 98% efficiency in ECO mode; Smart LCD screen; Intelligent slot; RS-232, USB port, and REPO connections; UL, cUL, RoHS approved; FCC Class B; TAA Compliant; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2" x 15.1" x 3.5"; 34.2 lbs | 1520
90000623 | P91-2000 | Xtreme Power P91 Series 2000VA/1930W; Online UPS; 2U; 120VAC; 6' input line cord with 5-20 plug; (8) 5-15/20R output receptacles, (4) of the output receptacles programmable as group; Hot Swappable batteries; 1-8A adjustable charger; Full Load Runtime = 3 min; Tower and rack mounting; 98% efficiency in ECO mode; Smart LCD screen; Intelligent slot; RS-232, USB port, and REPO connections; UL, cUL, RoHS approved; FCC Class A; TAA Compliant; 3 year full Warranty (USA and Cnada); 50K load protection policy; 17.2" x 19.0" x 3.5"; 43 lbs | 1985
90000624 | P91-3000 | Xtreme Power P91 Series 3000VA/2880W; Online UPS; 2U; 120VAC; 6' input line cord with L5-30 plug; (1) L5-30R + (6) 5-15/20R output receptacles, (3) of the 5-15/20R output receptacles programmable as group; Hot Swappable batteries; 1-8A adjustable charger; Full Load Runtime = 3 min; Tower and rack mounting; 98% efficiency in ECO mode; Smart LCD screen; Intelligent slot; RS-232, USB port, and REPO connections; UL, cUL, RoHS approved; FCC Class A; TAA Compliant; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2" x 23.8" x 3.5"; 60.6 lbs. | 2650
P91g 1-3K SERIES - 208/230 Volt with Lead Acid Batteries
Part Number | MODEL | DESCRIPTION | LIST PRICE
90000746 | P91gc-1000 | Xtreme Power P91 Series 1000VA/800W; Online UPS; 1U; 230 VAC, 200/208/220/230/240VAC selectable; C14 inlet with 8' C13 to L6-20P input line cord; (3) C13 output receptacle; Hot Swappable batteries; 1A charger; Full Load Runtime = 8 min; Front mount rack brackets included; 98% efficiency in ECO mode; Smart LED display; Intelligent slot; USB port connection; CE, RoHS; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2" x 17.8" x 1.7"; 28 lbs. | 1050
90000747 | P91g-1500 | Xtreme Power P91g Series 1500VA/1500W; Online UPS; 2U; 230 VAC, 200/208/220/230/240VAC selectable; IEC-C14 Inlet with 8' IEC C13 to L6-20P detachable input line cord; (8) IEC C13 output receptacles, (4) of the output receptacles programmable as group; Hot Swappable Batteries; 1-12A adjustible charger; Full Load Runtime = 3 min; Tower and rack mounting; 98% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; CE and RoHS approved; TAA Compliant; 3 year full Warranty (USA only); 50K load protection policy; 17.2" x 15.1" x 3.5". 34.2 lbs. Capacity derates 90% for 200 or 208 VAC output. | 1399
90000748 | P91g-2000 | Xtreme Power P91 Series 2000VA/2000W; Online UPS; 2U; 230VAC, 200/208/220/230/240VAC selectable ; IEC-C20 Inlet with 8' IEC C19 to L6-20P detachable input line cord; (8) IEC C13 output receptacles, (4) of the output receptacles programmable as group; Hot Swappable batteries; 1-12A adjustable charger; Full Load Runtime = 3 min; Tower and rack mounting; 98% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; CE, RoHS approved; TAA Compliant; 3 year full Warranty (USA and Cnada); 50K load protection policy; 17.2" x 19.0" x 3.5"; 43 lbs. Capacity derates 90% for 200 or 208 VAC output. | 1829
90000749 | P91g-3000 | Xtreme Power P91g Series 3000VA/3000W; Online UPS; 2U; 230VAC, 200/208/220/230/240VAC selectable ; IEC-C20 Inlet with 8' IEC C19 to L6-20P detachable input line cord; (1) C19 + (8) IEC C13 output receptacles, (4) of the output receptacles programmable as group; Hot Swappable batteries; 1-12A adjustable charger; Full Load Runtime = 3 min; Tower and rack mounting; up to 98% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; CE, RoHS approved; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2" x 23.8" x 3.5". 60.6 lbs. Capacity derates 90% for 200 or 208 VAC output. | 2449
P91 1-3K SERIES External Batteries and Accessories
Part Number | MODEL | DESCRIPTION | LIST PRICE
90000787 | P91-BP36 | Extended Runtime Battery Pack for use with P91(g)-1500 (includes 2 strings of 12V9AH batteries); __ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower or Rack Mounting; UL, cUL, RoHS Approved; 3-Year Full Warranty (USA and Canada); 17.2"W x 18.9"D x 3.5"H; 58.1 lbs | 920
90000788 | P91-BP36E | Extended Runtime Battery Pack for use with P91(g)-1500 (includes 4 strings of 12V9AH batteries); __ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower or Rack Mounting; UL, cUL, RoHS Approved; 3-Year Full Warranty (USA and Canada); 17.2"W x 23.6"D x 3.5"H; 104.4 lbs | 1320
90000789 | P91-BP48 | Extended Runtime Battery Pack for use with P91(g)-2000 UPS; (includes 2 strings of 12V9AH batteries); __ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower or Rack Mounting; UL, cUL, RoHS Approved; 3-Year Full Warranty (USA and Canada); 17.2"W x 18.9"D x 3.5"H; 74.6 lbs | 1080
90000790 | P91-BP72 | Extended Runtime Battery Pack for use with P91-3000 and P91g-3000 UPSs; (includes 2 strings of 12V9AH batteries) ;__ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower or Rack Mounting; UL, cUL, RoHS Approved; 3-Year Full Warranty (USA and Canada); 17.2"W x 23.6"D x 3.5"H; 104.4 lbs | 1290
TBD | XPC-C14-615R | P91g Output Cord, 1ft, IEC C14 to 6-15R. 3 lbs. | 45
TBD | XPC-C14-620R | P91g Output Cord, 1ft, IEC C14 to 6-20R. 3 lbs. | 49
TBD | XPC-C14-L620R | P91g Output Cord, 1ft, IEC C14 to L6-20R. 3 lbs. | 69
TBD | XPC-C14-L630R | P91g Output Cord, 1ft, IEC C14 to L6-30R. 3 lbs. | 69
| XPC-ZLC20-620R | Optional 12" output cord, Locking C20 to 6-15/20 receptacle; 3 lbs. | 79
| XPC-ZLC20-L620R | Optional 12" output cord, Locking C20 to L6-20 receptacle; 3 lbs. | 79
| XPC-ZLC20-L630R | Optional 12" output cord, Locking C20 to L6-30 receptacle; 3 lbs. | 79
90000909 | P90-RAIL | 4-Post Rail Kit for use with P91(g)-1000, 1500, 2000, 3000; extends from 18.75" to 30.9"; packaging 3.8"W x 19.8"D x 2.8"H. 5 lbs. | 135
90000406 | XPC-2PRAIL | 2-Post Rail Kit for P80, P91(g) and NXRT 800VA thru 5kVA UPS or EBM; rated for 125 lbs; 4"W x 20"D x 3"H. 5 lbs. | 102
90000116 | XPC-2POSTL | 2-Post Shelf Kit for P91(g)-1000, 1500, 2000, 3000; rated for 150lbs; 21.5"W x 23.3"D x 3.5"H. 9 lbs. | 160
90001273 | XPC-2PRLV2 | 2-Post Shelf Kit with front ears for P91(g)-1000, 1500, 2000, 3000; rated for 160lbs; 21.5"W x 23.3"D x 3.5"H. 9 lbs. | 225
90000392 | PV-WMB | Wall mount bracket for use with P80, P91(g) and P91L series UPSs and battery packs up to 5KVA; 4"W x 24"D x 4"H. 5 lbs. | 80
90000377 | P90-FRMB | Front Rackmount Bracket for P80 800VA through 2KVA size or P91 1KVA thru 2KVA size. Required when front mounting the UPS to a 2 post or 4 post rack with no rail kit. | 36
90000741 | SNMP-2PV3 | Internal SNMP/WEB Card for use with P80 or P91(g) Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-EMPV2 Environmental Monitor; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 359
90000674 | SNMP-EMPV2 | Environmental Monitoring Sensor to monitor room temperature and humidity - used with SNMP-2PV3 SNMP/WEB Card. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 230
90000267 | MODBUS-IN | MODBUS CARD for use with the P91(g) Series UPS; packaging = 7.25" x 6" x 2.5", 1 lbs | 319
90000265 | RELAY-MINI | Dry Contact RELAY CARD with DB9 & terminal block adapter; packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 120
90000090 | XBDM-1015LV | Xtreme Power XBDM Series 15 Amp Maintenance Bypass Distribution Module with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of BDM + (4) 5-15R output receptacles on rear of BDM; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads;3-Year Warranty (USA and Canada); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 379
90000091 | XBDM-1020LV | Xtreme Power XBDM Series 20 Amp Maintenance Bypass Distribution Module with 12' Input line cord with 5-20P plug; (6) 5-20R output receptacles on front of BDM + (4) 5-20R output receptacles on rear of BDM; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads; 3-Year Warranty (USA and Canada); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 419
90000093 | XBDM-1030LV | Xtreme Power XBDM Series 30 Amp Maintenance Bypass Distribution Module with 6' Input line cord with L5-30P plug; (5) 5-20R output receptacles on front of BDM (Load Group 1) + (5) 5-20R output receptacles on rear of BDM (Load Group 2); (2) bypass switches allowing for bypassing and maintenance of the UPS without affecting the connected loads; 3-Year Warranty (USA and Canada); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 659
90000041 | XPD1415HV | Xtreme Power XPDU Series Basic Power PDU with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of PDU + (8) 5-15R output receptacles on rear of PDU; UL60950-1/cUL/FCC Approved; 3-Year Warranty (USA and Canada); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 138
90000045 | XPD1420HV | Xtreme Power XPDU Series Basic Power PDU with 12' Input line cord with L5-20P plug (L5-20 to 5-20 adapter included); (6) 5-20R output receptacles on front of PDU + (8) 5-20R output receptacles on rear of PDU; UL60950-1/cUL/FCC Approved; 3-Year Warranty (USA and Canada); 19"W x 3.5"D x 1.75"H, 4.8 lbs | 190
90000094 | XBDM1020HV2 | Xtreme Power XBDM Series Maintenance Bypass Distribution Module with C20 input receptacle; rated at 16A; (2) IEC C19 and (4) IEC C13 output receptacles on front + (4) IEC C13 output receptacles on back; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads; Includes (2) IEC C20C19 cord kit; 3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 419
90000053 | XPDU-IEC | Xtreme Power XPDU Series Basic Power 230V PDU with C20 inlet (power cord ordered separately), (10) IEC C13 + (2) IEC C19 output receptacles; 1U Rackmount configuration; CE Listed; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 2.6 lbs | 190
90000269 | XAT-400 | 400VA Step Down Transformer, 208V to 120V for P90G and P90LG-3000. Input is 208V IEC C14 on 2ft cord; output is 120V 5-15R on 2ft cord. 7"W x 6.8"D x 5.9"H. 8 lbs. | 600
90000739 | XPD-IT15A | Xtreme Power XPDU Series PDU with Isolation Transformer. 1500W, 208V in, 120V out. IEC-C14 inlet with 3' 5-15 line cord ; (16) 5-15R output receptacles protected by 15A breaker; 3-Year Warranty; 17.5"W x 15"D x 3.5"H (2U), 43 lbs. | 980
90000877 | P915SP15 | Xtended 5YR Factory Warranty forP91c-1000, P91-1000, P91-1500 UPS (USA and Canada) - 5 Year Coverage includes coverage of electronics and internal batteries, telephone technical support, advanced exchange and ground shipping both ways. | 375
90000878 | P915SP23 | Xtended 5YR Factory Warranty for P91-2000/3000VA and P91g-3000 UPS (USA and Canada) - 5 Year Coverage includes coverage of electronics and internal batteries, telephone technical support, advanced exchange and ground shipping both ways. | 610
90000879 | P91L5SPBP | Xtended 5YR Factory Warranty for P91-BP36/BP36E/BP42/BP72 (USA and Canada) - 5 Year Coverage includes coverage of battery pack, telephone technical support, advanced exchange and ground shipping both ways.. | 320

## P91(g) 1.5-3k Lithium
|  | Return to Index | 2024-08-01
P91 1-3K SERIES - 120 Volt with Lithium-ion Batteries
Part Number | MODEL | DESCRIPTION | LIST PRICE
90000750 | P91-1.5KLi | Xtreme Power P91 Series 1500VA/1350W; Online UPS with Lithium-ion batteries; 2U; 120VAC; 6' input line cord with 5-15P; (8) 5-15R output receptacles, (4) of the output receptacles programmable as group; 1-8A adjustable charger; Full Load Runtime = 8 min; Tower and rack mounting; up to 98% efficiency in ECO mode; Smart LCD screen; Intelligent slot; RS-232 and USB port; REPO connection; UL, cUL, RoHS, FCC Class A, UN38.3 for battery transportation; 6 year full Warranty (USA and Canada), 1 year full Warranty (worldwide); 50K load protection policy; 17.2" x 15.1" x 3.5"; 25.6 lbs | 2520
90000751 | P91-2KLi | Xtreme Power P91 Series 2000VA/1800W; Online UPS with Lithium-ion batteries; 2U; 120VAC; 6' input line cord with 5-20 plug; (8) 5-15/20R output receptacles, (4) of the output receptacles programmable as group; 1-8A adjustable charger; Full Load Runtime = 14 min; Tower and rack mounting; 98% efficiency in ECO mode; Smart LCD screen; Intelligent slot, RS-232 and USB port connections; REPO connection; UL, cUL, RoHS, FCC Class A, UN38.3 for battery transportation; 6 year full Warranty (USA and Canada), 1 year full Warranty (worldwide); 50K load protection policy; 17.2" x 19.0" x 3.5"; 33.5 lbs | 3730
90000752 | P91-3kLi | Xtreme Power P91 Series 3000VA/2700W; Online UPS with Lithium-ion batteries; 2U; 120VAC; 6' input line cord with L5-30 plug; (1) L5-30R + (6) 5-15/20R output receptacles, (3) of the 5-15/20R output receptacles programmable as group; 1-8A adjustable charger; Full Load Runtime = 11 min; Tower and rack mounting; 98% efficiency in ECO mode; Smart LCD screen; Intelligent slot, RS-232 and USB port connections, REPO connection; UL, cUL, RoHS, FCC Class A, UN38.3 for battery transportation; 6 year full Warranty (USA and Canada); 50K load protection policy; 17.2" x 23.8" x 3.5"; 45.2 lbs. | 4570
P91g 1-3K SERIES - 208/230 Volt with Lithium-ion Batteries
Part Number | MODEL | DESCRIPTION | LIST PRICE
90000753 | P91g-1.5KLi | Xtreme Power P91 Series 1500VA/1350W; Online UPS with Lithium-ion batteries; 2U; 208/230VAC; C14 Inlet with 8' C13 to L6-20P line cord ; (8) IEC C13 output receptacles, (4) of the output receptacles programmable as group; 1-8A adjustable charger; Full Load Runtime = 8 min; Tower and rack mounting; up to 98% efficiency in ECO mode; Smart LCD screen; Intelligent slot; RS-232 and USB port; REPO connection; CE, RoHS, FCC Class A, UN38.3 for battery transportation; 6 year full Warranty (USA and Canada); 50K load protection policy; 17.2" x 15.1" x 3.5"; 25.6 lbs | 2470
90000754 | P91g-2KLi | Xtreme Power P91 Series 2000VA/1800W; Online UPS with Lithium-ion batteries; 2U; 208/230VAC; C20 Inlet with 8' C19 to L6-20P line cord ; (8) IEC C13 output receptacles (4) of the output receptacles programmable as group; 1-8A adjustable charger; Full Load Runtime = 14 min; Tower and rack mounting; 98% efficiency in ECO mode; Smart LCD screen; Intelligent slot, RS-232 and USB port connections; REPO connection; CE, RoHS, FCC Class A, UN38.3 for battery transportation; 6 year full Warranty (USA and Canada), 1 year full Warranty (worldwide); 50K load protection policy; 17.2" x 19.0" x 3.5"; 33.5 lbs | 3680
90000755 | P91g-3kLi | Xtreme Power P91 Series 3000VA/2700W; Online UPS with Lithium-ion batteries; 2U; 208/230VAC; C20 Inlet with 8' C19 to L6-20P line cord ; (1) IEC C19,(8) IEC C13 output receptacles, (4) of the C13 output receptacles programmable as group; 1-8A adjustable charger; Full Load Runtime = 11 min; Tower and rack mounting; 98% efficiency in ECO mode; Smart LCD screen; Intelligent slot, RS-232 and USB port connections, REPO connection; CE, RoHS, FCC Class A, UN38.3 for battery transportation; 6 year full Warranty (USA and Canada), 1 year full Warranty (worldwide); 50K load protection policy; 17.2" x 23.8" x 3.5"; 45.2 lbs. | 4520
TBD | XPC-C14-615R | P91g Output Cord, 1ft, IEC C14 to 6-15R. 3 lbs. | 45
TBD | XPC-ZLC20-620R | Optional 12" output cord, Locking C20 to 6-15/20 receptacle for use with P91g-3kLi; 3 lbs. | 79
TBD | XPC-ZLC20-L620R | Optional 12" output cord, Locking C20 to L6-20 receptacle for use with P91g-3kLi; 3 lbs. | 79
TBD | XPC-ZLC20-L630R | Optional 12" output cord, Locking C20 to L6-30 receptacle for use with P91g-3kLi; 3 lbs. | 79
90000909 | P90-RAIL | 4-Post Rail Kit for use with P91(g)-1000, 1500, 2000, 3000; extends from 18.75" to 30.9"; packaging 3.8"W x 19.8"D x 2.8"H. 5 lbs. | 135
90000406 | XPC-2PRAIL | 2-Post Rail Kit for P80, P91(g) and NXRT 800VA thru 5kVA UPS or EBM; rated for 125 lbs; 4"W x 20"D x 3"H. 5 lbs. | 102
90000116 | XPC-2POSTL | 2-Post Shelf Kit for P91(g)-1000, 1500, 2000, 3000; rated for 150lbs; 21.5"W x 23.3"D x 3.5"H. 9 lbs. | 160
90001273 | XPC-2PRLV2 | 2-Post Shelf Kit with front ears for P91(g) Li; rated for 160lbs; 21.5"W x 23.3"D x 3.5"H. 9 lbs. | 225
90000392 | PV-WMB | Wall mount bracket for use with P80, P91(g) and P91L series UPSs and battery packs up to 5KVA; 4"W x 24"D x 4"H. 5 lbs. | 80
90000377 | P90-FRMB | Front Rackmount Bracket for P80 800VA through 2KVA size or P91 1KVA thru 2KVA size. Required when front mounting the UPS to a 2 post or 4 post rack with no rail kit. | 36
90000741 | SNMP-2PV3 | Internal SNMP/WEB Card for use with P80 or P91(g) Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-EMPV2 Environmental Monitor; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 359
90000674 | SNMP-EMPV2 | Environmental Monitoring Sensor to monitor room temperature and humidity - used with SNMP-2PV3 SNMP/WEB Card. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 230
90000267 | MODBUS-IN | MODBUS CARD for use with the P91(g) Series UPS; packaging = 7.25" x 6" x 2.5", 1 lbs | 319
90000265 | RELAY-MINI | Dry Contact RELAY CARD with DB9 & terminal block adapter; packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 120
90000090 | XBDM-1015LV | Xtreme Power XBDM Series 15 Amp Maintenance Bypass Distribution Module with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of BDM + (4) 5-15R output receptacles on rear of BDM; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads;3-Year Warranty (USA and Canada); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 379
90000091 | XBDM-1020LV | Xtreme Power XBDM Series 20 Amp Maintenance Bypass Distribution Module with 12' Input line cord with 5-20P plug; (6) 5-20R output receptacles on front of BDM + (4) 5-20R output receptacles on rear of BDM; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads; 3-Year Warranty (USA and Canada); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 419
90000093 | XBDM-1030LV | Xtreme Power XBDM Series 30 Amp Maintenance Bypass Distribution Module with 6' Input line cord with L5-30P plug; (5) 5-20R output receptacles on front of BDM (Load Group 1) + (5) 5-20R output receptacles on rear of BDM (Load Group 2); (2) bypass switches allowing for bypassing and maintenance of the UPS without affecting the connected loads; 3-Year Warranty (USA and Canada); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 659
90000041 | XPD1415HV | Xtreme Power XPDU Series Basic Power PDU with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of PDU + (8) 5-15R output receptacles on rear of PDU; UL60950-1/cUL/FCC Approved; 3-Year Warranty (USA and Canada); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 138
90000045 | XPD1420HV | Xtreme Power XPDU Series Basic Power PDU with 12' Input line cord with L5-20P plug (L5-20 to 5-20 adapter included); (6) 5-20R output receptacles on front of PDU + (8) 5-20R output receptacles on rear of PDU; UL60950-1/cUL/FCC Approved; 3-Year Warranty (USA and Canada); 19"W x 3.5"D x 1.75"H, 4.8 lbs | 190
90000094 | XBDM1020HV2 | Xtreme Power XBDM Series Maintenance Bypass Distribution Module with C20 input receptacle; rated at 16A; (2) IEC C19 and (4) IEC C13 output receptacles on front + (4) IEC C13 output receptacles on back; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads; Includes (2) IEC C20C19 cord kit; 3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 419
90000053 | XPDU-IEC | Xtreme Power XPDU Series Basic Power 230V PDU with C20 inlet (power cord ordered separately), (10) IEC C13 + (2) IEC C19 output receptacles; 1U Rackmount configuration; CE Listed; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 2.6 lbs | 190
90000269 | XAT-400 | 400VA Step Down Transformer, 208V to 120V for P90G and P90LG-3000. Input is 208V IEC C14 on 2ft cord; output is 120V 5-15R on 2ft cord. 7"W x 6.8"D x 5.9"H. 8 lbs. | 600
90000739 | XPD-IT15A | Xtreme Power XPDU Series PDU with Isolation Transformer. 1500W, 208V in, 120V out. IEC-C14 inlet with 3' 5-15 line cord ; (16) 5-15R output receptacles protected by 15A breaker; 3-Year Warranty; 17.5"W x 15"D x 3.5"H (2U), 43 lbs.. | 980
90001036 | P91ADVEX | Advanced Exchange Warranty Upgrade for advanced warranty exchange and shipping for P91(g)-1.5kLi, P91(g)-2kLi, and P91(g)-3kLi UPS (USA and Canada) | 250

## P90L(g) 1-3K
|  | Return to Index | 2024-08-01
P90L 1.5-3K Series Double Conversion UPS
90000912 | P90L-1500 | Xtreme Power P90L Series 1250VA/1125W; Online UPS; 2U; 120VAC; 6A charger w/ no internal batteries; 6' input line cord with 5-15 plug; (8) 5-15R output receptacles; Tower and rack mounting; 98% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; UL, cUL, RoHS approved; TAA Compliant; 3 year full Warranty (USA only); 50K load protection policy; 17.2" x 18.9" x 3.5"; 33 lbs | 1450
90000913 | P90L-2000 | Xtreme Power P90L Series 1700VA/1530W; Online UPS; 2U; 120VAC; 6A charger w/ no internal batteries; 6' input line cord with 5-20 plug; (8) 5-15/20R output receptacles; Tower and rack mounting; 98% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; UL, cUL, RoHS approved; TAA Compliant; 3 year full Warranty (USA only); 50K load protection policy; 17.2" x 18.9" x 3.5"; 35 lbs | 1675
90000914 | P90L-3000 | Xtreme Power P90L Series 2500VA/2250W; Online UPS; 2U; 120VAC; 6A charger w/ no internal batteries; 6' input line cord with L5-30 plug; (1) L5-30R + (4) 5-15/20R output receptacles; Tower and rack mounting; 98% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; UL, cUL, RoHS approved; TAA Compliant; 3 year full Warranty (USA only); 50K load protection policy; 17.2" x 25.8" x 3.5"; 47 lbs | 2525
90000921 | P90Lg-3000 | Xtreme Power P90L Series 3000VA/2400W; Online UPS; 2U; 208-240VAC; 6A charger w/ no internal batteries; IEC C20 to L6-20P detachable input line cord (8 ft); (1)IEC-C19 + (6) IEC-C13 output receptacles; Tower and rack mounting; 98% efficiency in ECO mode; Smart LCD screen; RS-232 and USB port connections; CE and RoHS approved; TAA Compliant; 3 year full Warranty (USA only); 50K load protection policy; 17.2" x 25.8" x 3.5"; 47 lbs | 2490
90000915 | P90-BP36 | Extended Runtime Battery Pack for use with P90/P90L-1500 (includes 6 each 12V9AH batteries); __ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower or Rack Mounting; TUV/UL, RoHS, cUL Approved; TAA Compliant; 3-Year Full Warranty (USA only); 17.2"W x 18.9"D x 3.5"H; 58.1 lbs | 920
90000923 | P90-BP36E | Extended Runtime Battery Pack for use with P90/P90L-1500 (includes 12 each 12V9AH batteries); __ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower or Rack Mounting; TUV/UL, RoHS, cUL Approved; TAA Compliant; 3-Year Full Warranty (USA only); 17.2"W x 23.6"D x 3.5"H; 104.4 lbs | 1320
90000916 | P90-BP48 | Extended Runtime Battery Pack for use with P80-1500, P80-2000, P90 and P90L-2000 UPSs; (includes 8 each 12V9AH batteries); __ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower or Rack Mounting; TUV/UL, RoHS, cUL Approved; TAA Compliant; 3-Year Full Warranty (USA only); 17.2"W x 18.9"D x 3.5"H; 74.6 lbs | 990
90000917 | P90-BP72 | Extended Runtime Battery Pack for use with P90/ P90L-3000 and P90g/P90Lg-3000 UPSs; (includes 12 each 12V9AH batteries) ;__ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower or Rack Mounting; TUV/UL, RoHS, cUL Approved; TAA Compliant; 3-Year Full Warranty (USA only); 17.2"W x 23.6"D x 3.5"H; 104.4 lbs | 1290
TBD | XPC-C14-615R | P91g Output Cord, 1ft, IEC C14 to 6-15R. 3 lbs. | 49
TBD | XPC-ZLC20-620R | Optional 12" output cord, Locking C20 to 6-15/20 receptacle for use with TX91; 3 lbs. | 79
TBD | XPC-ZLC20-L620R | Optional 12" output cord, Locking C20 to L6-20 receptacle for use with TX91; 3 lbs. | 79
TBD | XPC-ZLC20-L630R | Optional 12" output cord, Locking C20 to L6-30 receptacle for use with TX91; 3 lbs. | 79
90000909 | P90-RAIL | Adjustable Mounting 4-Post Rail Kit for P90L-1500/2000/3000 and P90-BP36/48/72; extends from 18.75" to 30.9"; packaging 3.8"W x 19.8"D x 2.8"H, 5 lbs | 135
90000406 | XPC-2PRAIL | 2-Post Rail Kit for P80, P90, P90L and NXRT 800VA thru 5kVA UPS or EBM; rated for 125 lbs; 4"W x 20"D x 3"H. 5 lbs. | 102
90000116 | XPC-2POSTL | 2-Post Shelf Kit for P90L-1500/2000/3000 and P90-BP36/48/72; 21/5"W x 23.3"D x 3.5"H. 9 lbs | 160
90000741 | SNMP-2PV3 | Internal SNMP/WEB Card for use with P80 or P90 Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-EMPv2 Environmental Monitor; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 359
90000674 | SNMP-EMPV2 | Environmental Monitoring Sensor to monitor room temperature and humidity - used with SNMP-2PV3 SNMP/WEB Card. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 230
90000265 | RELAY-MINI | Dry Contact RELAY CARD with DB9 & terminal block adapter; packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 120
90000267 | MODBUS-IN | MODBUS CARD for use with the P90L Series UPS; packaging = 7.25" x 6" x 2.5", 1 lbs | 319
90000090 | XBDM-1015LV | Xtreme Power XBDM Series 15 Amp Maintenance Bypass Distribution Module with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of BDM + (4) 5-15R output receptacles on rear of BDM; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads;3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 379
90000091 | XBDM-1020LV | Xtreme Power XBDM Series 20 Amp Maintenance Bypass Distribution Module with 12' Input line cord with 5-20P plug; (6) 5-20R output receptacles on front of BDM + (4) 5-20R output receptacles on rear of BDM; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads; 3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 419
90000093 | XBDM-1030LV | Xtreme Power XBDM Series 30 Amp Maintenance Bypass Distribution Module with 6' Input line cord with L5-30P plug; (5) 5-20R output receptacles on front of BDM (Load Group 1) + (5) 5-20R output receptacles on rear of BDM (Load Group 2); (2) bypass switches allowing for bypassing and maintenance of the UPS without affecting the connected loads; 3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 659
90000094 | XBDM1020HV2 | Xtreme Power XBDM Series Maintenance Bypass Distribution Module with C20 inlet for customer supplied power cord; rated at 16A; (2) IEC C19 and (4) IEC C13 output receptacles on front + (4) IEC C13 output receptacles on back; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads; Includes (2) IEC C20 to C19 cord kits for connecting the XBDM to the P90G-3000 or P90LG-3000 UPS; 3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 419
90000041 | XPD1415HV | Xtreme Power XPDU Series Basic Power PDU with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of PDU + (8) 5-15R output receptacles on rear of PDU; UL60950-1/cUL/FCC Approved; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 3.5 lbs | 138
90000045 | XPD1420HV | Xtreme Power XPDU Series Basic Power PDU with 12' Input line cord with L5-20P plug (L5-20 to 5-20 adapter included); (6) 5-20R output receptacles on front of PDU + (8) 5-20R output receptacles on rear of PDU; UL60950-1/cUL/FCC Approved; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 4.8 lbs | 190
90000053 | XPDU-IEC | Xtreme Power XPDU Series Basic Power 230V PDU with C20 inlet (power cord ordered separately), (10) IEC C13 + (2) IEC C19 output receptacles; 1U Rackmount configuration; CE Listed; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 2.6 lbs | 190
90000739 | XPD-IT15A | Xtreme Power XPDU Series PDU with Isolation Transformer. 1500W, 208V in, 120V out. IEC-C14 inlet with 3' 5-15 line cord ; (16) 5-15R output receptacles protected by 15A breaker; 3-Year Warranty; 17.5"W x 15"D x 3.5"H (2U), 43 lbs. | 980
90000269 | XAT-400 | 400VA Step Down Transformer, 208V to 120V for P90g and P90Lg-3000. Input is 208V IEC C14 on 2ft cord; output is 120V 5-15R on 2ft cord. 7"W x 6.8"D x 5.9"H. 8 lbs. | 600
90000527 | P90L5SP15 | Xtended 5YR Factory Warranty for P90L 1500VA (USA only) - 5 Year Coverage includes coverage of electronics, telephone technical support, advanced exchange and ground shipping both ways.. | 370
90000528 | P90L5SP23 | Xtended 5YR Factory Warranty for P90L 2000/3000VA and P90Lg-3000 (USA only) - 5 Year Coverage includes coverage of electronics, telephone technical support, advanced exchange and ground shipping both ways.. | 610
90000524 | P90L5SPBP | Xtended 5YR Factory Warranty for P90L-BP36/BP42/BP72 (USA only) - 5 Year Coverage includes coverage of battery pack, telephone technical support, advanced exchange and ground shipping both ways.. | 320

## T91
|  | Return to Index | 2024-08-01
T91 Series Double Conversion 700VA-3KVA UPS
Part Number | MODEL | DESCRIPTION | LIST PRICE
90000480 | T91-700 | Xtreme Power T91 Series 700VA/700W Online UPS, 120VAC; 6' Input line cord with 5-15P plug; (6) 5-15R output receptacles; Full Load Runtime = 6 minutes; ECO Mode; 2A to 8A charger current adjustable by LCD; Tower; RS232/USB Port; Emergency Power Off (EPO); Includes USB Cable and ViewPower Software; UL/cUL/FCC/RoHS Approved; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada only); 5.6"W x 15.6"D x 8.6"H, 25.7 lbs; | 769
90000481 | T91-1000 | Xtreme Power T91 Series 1000VA/1000W Online UPS, 120VAC; 6' Input line cord with 5-15P plug; (6) 5-15R output receptacles; Full Load Runtime = 7 minutes; ECO Mode; 2A to 8A charger current adjustable by LCD; Tower; RS232/USB Port; Emergency Power Off (EPO); Includes Communications Cable and ViewPower Software; UL/cUL/FCC/RoHS Approved; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada only); 5.6"W x 15.6"D x 8.6"H, 30 lbs; | 949
90000482 | T91-1500 | Xtreme Power T91 Series 1500VA/1450W Online UPS, 120VAC; 6' Input line cord with 5-15P plug; (6) 5-15R output receptacles; Full Load Runtime = 3 minutes; ECO Mode; 2A to 8A charger current adjustable by LCD; Tower; RS232/USB Port; Emergency Power Off (EPO); Includes Communications Cable and ViewPower Software; UL/FCC/RoHS Approved; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA only); 5.6"W x 15.6"D x 8.6"H, 34.3 lbs; | 1149
90000483 | T91-2000 | Xtreme Power T91 Series 2000VA/1930W Online UPS, 120VAC; 6' Input line cord, L5-20P; (1) L5-20R and (8) 5-20R output receptacles; Full Load Runtime = 7 minutes; ECO Mode; 2A to 8A charger current adjustable by LCD; Tower; RS232/USB Port; Emergency Power Off (EPO); Includes Communications Cable and ViewPower Software; UL/cUL/FCC/RoHS Approved; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada only); 7.4"W x 16.5"D x 12.5"H, 63 lbs; | 1539
90001242 | T91-2000V2 | Xtreme Power T91 Series 2000VA/1930W Online UPS, 120VAC; 6' Input line cord, 5-20P; (1) L5-20R and (8) 5-20R output receptacles; Full Load Runtime = 7 minutes; ECO Mode; 2A to 8A charger current adjustable by LCD; Tower; RS232/USB Port; Emergency Power Off (EPO); Includes Communications Cable and ViewPower Software; UL/cUL/FCC/RoHS Approved; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada only); 7.4"W x 16.5"D x 12.5"H, 63 lbs; | 1539
90000485 | T91i-2000 | Xtreme Power T91i Series 2000VA/2000W Online UPS, 208-240VAC; IEC-C20 Inlet; (1) IEC-C19 and (8) IEC-C13 output receptacles; Full Load Runtime = 6 minutes; ECO Mode; 2A to 8A charger current adjustable by LCD; Tower; RS232/USB Port; Emergency Power Off (EPO); Includes USB Cable and ViewPower Software; CE, RoHS Approved; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada only); 7.4"W x 16.5"D x 12.5"H (190mmW x 421mmD x 318mmH) , 62 lbs; | 1629
90000484 | T91-3000 | Xtreme Power T91 Series 3000VA/2880W Online UPS, 120VAC; 6' Input line cord L5-30P; (1) L5-30R and (8) 5-15/20R output receptacles; Full Load Runtime = 3 minutes; ECO Mode; 2A to 8A charger current adjustable by LCD; Tower; RS232/USB Port; Emergency Power Off (EPO); Includes Communications Cable and ViewPower Software; UL/FCC/RoHS Approved; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada only); 7.4"W x 16.5"D x 12.5"H, 82 lbs; | 1979
90001214 | T91i-3000 | Xtreme Power T91i Series 3000VA/3000W Online UPS, 208/230VAC; IEC-C20 Inlet; (1) IEC-C19 and (8) IEC-C13 output receptacles; Full Load Runtime = 2 minutes; ECO Mode; 2A to 8A charger current adjustable by LCD; Tower; RS232/USB Port; Emergency Power Off (EPO); Includes USB Cable and ViewPower Software; CE, RoHS Approved; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada only); 7.4"W x 16.5"D x 12.5"H (190mmW x 421mmD x 318mmH) , 62 lbs; | 2149
90000486 | T91-BP36A | Extended Runtime Battery Pack (2 strings) for use with T91-1000, and T91-1500 (maximum 7 BP per UPS); __ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower; UL/FCC/RoHS Approved; TAA Compliant; 3-Year Battery Warranty (USA and Canada only); 5.6"W x 15.6"D x 8.6"H, 44 lbs | 699
90000487 | T91-BP72A | Extended Runtime Battery Pack (2 strings) for use with T91-2000, T91i-2000 and T91-3000 (maximum 7 BP per UPS); __ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower; UL/FCC/RoHS Approved; TAA Compliant; 3-Year Battery Warranty (USA and Canada only); 7.4"W x 16.5"D x 12.5"H, 82 lbs | 1259
90000741 | SNMP-2PV3 | Internal SNMP/WEB Card for use with P80 or P90 Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-EMPV2 Environmental Monitor; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 359
90000674 | SNMP-EMPV2 | Environmental Monitoring Sensor to monitor room temperature and humidity - used with SNMP-2PV3 SNMP/WEB Card. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 230
90000267 | MODBUS-IN | MODBUS CARD for use with the P90 Series UPS; packaging = 7.25" x 6" x 2.5", 1 lbs | 319
90000265 | RELAY-MINI | Dry Contact RELAY CARD with DB9 & terminal block adapter; packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 120
90000389 | T90-WMB | Wall mount bracket for use with T91-700 thru 1500 UPS. Compatible with any brick shaped UPS, between 4" and 8" wide. Rated for 40 lbs. 4.0" to 8.0 adjustable W x 7.0"D x 8.0"H. 5 lbs. | 219
90000269 | XAT-400 | 400VA Step Down Transformer, 208V to 120V for P90G and P90LG-3000. Input is 208V IEC C14 on 2ft cord; output is 120V 5-15R on 2ft cord. 7"W x 6.8"D x 5.9"H. 8 lbs. | 600
90000488 | T915SP715 | Xtended 5YR Factory Warranty for T91 1000/1500VA UPS (USA only) - 5 Year Coverage includes coverage of electronics and internal batteries, telephone technical support, advanced exchange and ground shipping both ways. | 350
90000489 | T915SP23 | Xtended 5YR Factory Warranty for T91 2000/3000VA UPS (USA only) - 5 Year Coverage includes coverage of electronics and internal batteries, telephone technical support, advanced exchange and ground shipping both ways. | 575
90000490 | T915SPBP | Xtended 5YR Factory Warranty for T91-BP1 and T91BP2 Extended Battery Packs (USA only) - 5 Year Coverage includes coverage of battery pack, telephone technical support, advanced exchange and ground shipping both ways. | 320

## P91 5-10K
|  | Return to Index | 2025-11-01
P91 SERIES 5, 6 & 10KVA 208/230V Bundled Solutions
Part Number | MODEL | DESCRIPTION | LIST PRICE
Bundle | P91-5KB | Xtreme Power P91- 5KVA/5KW online double conversion UPS in 4U total rack/tower configuration; 208-240VAC input and output; battery pack providing hot swappable battery trays and 7 minutes runtime at 5KW load; Terminal blocks for hardwired input and output; LCD display; intelligent slot for optional cards, RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 27.4"; Total Wt 163 lbs. Package Includes: P91-5k UPS Power Module (2U), BPXR2U240A Battery Module (2U), Tower Stands, Software; (2) 4 Post Rail Kits | 4658
Bundle | P91-5KB1 | Xtreme Power P91- 5KVA/5KW online double conversion UPS in 4U total rack/tower configuration; 208-240VAC input and output; Bypass distribution module, 2U battery pack providing hot swappable battery trays and 7 minutes runtime at 5KW load; input 6ft L6-30P line cord ; output (2) L6-30R, and (2) L6-20R receptacles; LCD display; intelligent slot for optional cards, RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 173 lbs. Package Includes: P91-5k UPS Power Module (2U), BPXR2U240A Battery Module (2U), XBDM-P91A Bypass PDU (0U) Tower Stands, Software; (2) 4 Post Rail Kits | 5546
Bundle | P91-5KB2 | Xtreme Power P91- 5KVA/5KW online double conversion UPS in 5U total rack/tower configuration; 208-240VAC input and output; battery pack providing hot swappable battery trays and 15 minutes runtime at 5KW load; Terminal blocks for hardwired input and output; LCD display; intelligent slot for optional cards, RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 27.4"; Total Wt 203 lbs. Package Includes: P91-5k UPS Power Module (2U), BPXR3U240A Battery Module (3U), Tower Stands, Software; (2) 4 Post Rail Kits | 5078
Bundle | P91-5KB3 | Xtreme Power P91- 5KVA/5KW online double conversion UPS in 5U total rack/tower configuration; 208-240VAC input and output; Bypass distribution module, 3U battery pack providing hot swappable battery trays and 15 minutes runtime at 5KW load; input 6ft L6-30P line cord ; output (2) L6-30R, and (2) L6-20R receptacles; LCD display; intelligent slot for optional cards, RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 213 lbs. Package Includes: P91-5k UPS Power Module (2U), BPXR3U240A Battery Module (3U), XBDM-P91A Bypass PDU (0U) Tower Stands, Software; (2) 4 Post Rail Kits | 5966
Bundle | P91-6KB | Xtreme Power P91- 6KVA/6KW online double conversion UPS in 4U total rack/tower configuration; 208-240VAC input and output; battery pack providing hot swappable battery trays and 5 minutes runtime at 6KW load; Terminal blocks for hardwired input and output; LCD display; intelligent slot for optional cards; RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 27.4"; Total Wt 164 lbs. Package Includes: P91-6k UPS Power Module (2U), BPXR2U240A Battery Module (2U), Tower Stands, Software; (2) 4 Post Rail Kits | 5048
Bundle | P91-6KB1 | Xtreme Power P91- 6KVA/6KW online double conversion UPS in 4U total rack/tower configuration; 208-240VAC input and output; Bypass distribution module, 2U battery pack providing hot swappable battery trays and 5 minutes runtime at 6KW load; input 6ft L6-30P line cord ; output (2) L6-30R, and (2) L6-20R receptacles; LCD display; intelligent slot for optional cards; RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 174 lbs. Package Includes: P91-6k UPS Power Module (2U), BPXR2U240A Battery Module (2U), XBDM-P91A Bypass PDU (0U) Tower Stands, Software; (2) 4 Post Rail Kits | 5936
Bundle | P91-6KB2 | Xtreme Power P91- 6KVA/6KW online double conversion UPS in 5U total rack/tower configuration; 208-240VAC input and output; battery pack providing hot swappable battery trays and 12 minutes runtime at 6KW load; Terminal blocks for hardwired input and output; LCD display; intelligent slot for optional cards; RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 27.4"; Total Wt 204 lbs. Package Includes: P91-6k UPS Power Module (2U), BPXR3U240A Battery Module (3U), Tower Stands, Software; (2) 4 Post Rail Kits | 5468
Bundle | P91-6KB3 | Xtreme Power P91- 6KVA/6KW online double conversion UPS in 5U total rack/tower configuration; 208-240VAC input and output; Bypass distribution module, 3U battery pack providing hot swappable battery trays and 12 minutes runtime at 6KW load; input 6ft L6-30P line cord ; output (2) L6-30R, and (2) L6-20R receptacles; LCD display; intelligent slot for optional cards; RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 214 lbs. Package Includes: P91-6k UPS Power Module (2U), BPXR3U240A Battery Module (3U), XBDM-P91A Bypass PDU (0U) Tower Stands, Software; (2) 4 Post Rail Kits | 6356
Bundle | P91-10KB | Xtreme Power P91- 10KVA/10KW online double conversion UPS in 5U total rack/tower configuration; 208-240VAC input and output; 3U battery pack providing hot swappable battery trays and 6 minutes runtime at 10KW load; Terminal blocks for hardwired input and output; LCD display; intelligent slot for optional cards; RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 27.4"; Total Wt 210 lbs. Package Includes: P91-10k UPS Power Module (2U), BPXR3U240A Battery Module (3U), Tower Stands, Software; (2) 4 Post Rail Kits | 6548
Bundle | P91-10KB1 | Xtreme Power P91- 10KVA/10KW online double conversion UPS in 5U total rack/tower configuration; 208-240VAC input and output; Bypass distribution module, 3U battery pack providing hot swappable battery trays and 6 minutes runtime at 10KW load; Hardwired Terminal Block input, output (1) L6-30R, (2) L6-20R receptacles and terminal blocks; LCD display; intelligent slot for optional cards; RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 218 lbs. Package Includes: P91-10k UPS Power Module (2U), BPXR3U240A Battery Module (3U), XBDM-P91B Bypass PDU (0U) Tower Stands, Software; (2) 4 Post Rail Kits | 7436
Bundle | P91-10KB2 | Xtreme Power P91- 10KVA/10KW online double conversion UPS in 4U total rack/tower configuration; 208-240VAC input and output; 2U battery pack providing hot swappable battery trays and 2 minutes runtime at 10KW load; Terminal blocks for hardwired input and output; LCD display; intelligent slot for optional cards; RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 27.4"; Total Wt 170 lbs. Package Includes: P91-10k UPS Power Module (2U), BPXR2U240A Battery Module (2U), Tower Stands, Software; (2) 4 Post Rail Kits | 6128
Bundle | P91-10KB3 | Xtreme Power P91- 10KVA/10KW online double conversion UPS in 4U total rack/tower configuration; 208-240VAC input and output; Bypass distribution module, 4U battery pack providing hot swappable battery trays and 2 minutes runtime at 10KW load; Hardwired Terminal Block input, output (1) L6-30R, (2) L6-20R receptacles and terminal blocks; LCD display; intelligent slot for optional cards; RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 178 lbs. Package Includes: P91-10k UPS Power Module (2U), BPXR2U240A Battery Module (2U), XBDM-P91B Bypass PDU (0U) Tower Stands, Software; (2) 4 Post Rail Kits | 7016
P91 SERIES 5, 6 & 10KVA 208-240 Input and 208/104 or 240/120V Output Bundled Solutions
Part Number | MODEL | DESCRIPTION | LIST PRICE
Bundle | P91-5KTB | Xtreme Power P91- 5KVA/5KW online double conversion UPS in 6U total rack/tower configuration; 208/240VAC input and 208/104V or 240/120V output; Bypass distribution module, 6kVA isolation transformer, battery pack providing hot swappable battery trays and 7 minutes runtime at 5KW load; input 6ft L6-30P line cord; output (2) L6-30R, (2) L6-20R and (12) 5-15/20R receptacles (6KW max 120V capability); LCD display; intelligent slot for optional cards, RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 315 lbs. Package Includes: P91-5k UPS Power Module (2U), BPXR2U240A Battery Module (2U), XBDM-P91A Bypass PDU (0U) (2) XPC-ZLC20-L6-20R XPD-IT60A Isolation Transformer (2U), Tower Stands, Software; (3) 4 Post Rail Kits | 7445
Bundle | P91-5KTB2 | Xtreme Power P91- 5KVA/5KW online double conversion UPS in 7U total rack/tower configuration; 208/240VAC input and 208/104V or 240/120V output; Bypass distribution module, 6kVA isolation transformer, battery pack providing hot swappable battery trays and 7 minutes runtime at 5KW load; input terminal block and 6ft L6-30P line cord; output Terminal block and (1) L6-30R, (2) L14-30R and (8) 5-15/20R receptacles; LCD display; intelligent slot for optional cards, RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 315 lbs. Package Includes: P91-5k UPS Power Module (2U), BPXR2U240A Battery Module (2U), XBDM-P91C Bypass PDU (0U) XPC-L630 Line Cord XPD-IT6KW Isolation Transformer (3U), Tower Stands, Software; (3) 4 Post Rail Kits | 7847
Bundle | P91-5KTB3 | Xtreme Power P91- 5KVA/5KW online double conversion UPS in 7U total rack/tower configuration; 208/240VAC input and 208/104V or 240/120V output; Bypass distribution module, 6kVA isolation transformer, battery pack providing hot swappable battery trays and 15 minutes runtime at 5KW load; input 6ft L6-30P line cord; output (2) L6-30R, (2) L6-20R and (12) 5-15/20R receptacles (6KW max 120V capability); LCD display; intelligent slot for optional cards, RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 355.1 lbs. Package Includes: P91-5k UPS Power Module (2U), BPXR3U240A Battery Module (3U), XBDM-P91A Bypass PDU (0U) (2) XPC-ZLC20-L6-20R XPD-IT60A Isolation Transformer (2U), Tower Stands, Software; (3) 4 Post Rail Kits | 7865
Bundle | P91-5KTB4 | Xtreme Power P91- 5KVA/5KW online double conversion UPS in 8U total rack/tower configuration; 208/240VAC input and 208/104V or 240/120V output; Bypass distribution module, 6kVA isolation transformer, battery pack providing hot swappable battery trays and 15 minutes runtime at 5KW load; input terminal block and 6ft L6-30P line cord; output Terminal block and (1) L6-30R, (2) L14-30R and (8) 5-15/20R receptacles ; LCD display; intelligent slot for optional cards, RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 355.1 lbs. Package Includes: P91-5k UPS Power Module (2U), BPXR3U240A Battery Module (3U), XBDM-P91C Bypass PDU (0U) XPC-L630 Line Cord XPD-IT6KW Isolation Transformer (3U), Tower Stands, Software; (3) 4 Post Rail Kits | 8267
Bundle | P91-6KTB | Xtreme Power P91- 6KVA/6KW online double conversion UPS in 6U total rack/tower configuration; 208/240VAC input and 208/104V or 240/120V output; Bypass distribution module, 6kVA isolation transformer, battery pack providing hot swappable battery trays and 5 minutes runtime at 6KW load; input 6ft L6-30P line cord; output (2) L6-30R, (2) L6-20R and (12) 5-15/20R receptacles (6KW max 120V capability); LCD display; intelligent slot for optional cards; RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 316 lbs. Package Includes: P91-6k UPS Power Module (2U), BPXR2U240A Battery Module (2U), XBDM-P91A Bypass PDU (0U) (2) XPC-ZLC20-L6-20R XPD-IT60A Isolation Transformer (2U), Tower Stands, Software; (3) 4 Post Rail Kits | 7835
Bundle | P91-6KTB2 | Xtreme Power P91- 6KVA/6KW online double conversion UPS in 7U total rack/tower configuration; 208/240VAC input and 208/120V or 240/120V output; Bypass distribution module, 6kVA isolation transformer, battery pack providing hot swappable battery trays and 5 minutes runtime at 6KW load; input terminal block and 6ft L6-30P line cord; output Terminal block and (1) L6-30R, (2) L14-30R and (8) 5-15/20R receptacles; LCD display; intelligent slot for optional cards, RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 316 lbs. Package Includes: P91-6k UPS Power Module (2U), BPXR2U240A Battery Module (2U), XBDM-P91C Bypass PDU (0U) XPC-L630 Line Cord XPD-IT6KW Isolation Transformer (3U), Tower Stands, Software; (3) 4 Post Rail Kits | 8237
Bundle | P91-6KTB3 | Xtreme Power P91- 6KVA/6KW online double conversion UPS in 7U total rack/tower configuration; 208/240VAC input and 208/104V or 240/120V output; Bypass distribution module, 6kVA isolation transformer, battery pack providing hot swappable battery trays and 12 minutes runtime at 6KW load; input 6ft L6-30P line cord; output (2) L6-30R, (2) L6-20R and (12) 5-15/20R receptacles (6KW max 120V capability); LCD display; intelligent slot for optional cards; RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 356 lbs. Package Includes: P91-6k UPS Power Module (2U), BPXR3U240A Battery Module (3U), XBDM-P91A Bypass PDU (0U) (2) XPC-ZLC20-L6-20R XPD-IT60A Isolation Transformer (2U), Tower Stands, Software; (3) 4 Post Rail Kits | 8255
Bundle | P91-6KTB4 | Xtreme Power P91- 6KVA/6KW online double conversion UPS in 8U total rack/tower configuration; 208/240VAC input and 208/120V or 240/120V output; Bypass distribution module, 6kVA isolation transformer, battery pack providing hot swappable battery trays and 12 minutes runtime at 6KW load; input terminal block and 6ft L6-30P line cord; output Terminal block and (1) L6-30R, (2) L14-30R and (8) 5-15/20R receptacles; LCD display; intelligent slot for optional cards, RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 356 lbs. Package Includes: P91-6k UPS Power Module (2U), BPXR3U240A Battery Module (3U), XBDM-P91C Bypass PDU (0U) XPC-L630 Line Cord XPD-IT6KW Isolation Transformer (3U), Tower Stands, Software; (3) 4 Post Rail Kits | 8675
Bundle | P91-10KTB | Xtreme Power P91- 10KVA/10KW online double conversion UPS in 7U total rack/tower configuration; 208/240VAC input and 208/104V or 240/120V output; Bypass distribution module, 6kVA isolation transformer, 3U battery pack providing hot swappable battery trays and 6 minutes runtime at 10KW load; hardwire terminal block input; output (1) L6-30R, (2) L6-20R and (12) 5-15/20R receptacles (6KW max 120V capability); LCD display; intelligent slot for optional cards; RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 360 lbs. Package Includes: P91-10k UPS Power Module (2U), BPXR3U240A Battery Module (3U), XBDM-P91B Bypass PDU (0U) XPD-IT60A Isolation Transformer (2U), Tower Stands, Software; (3) 4 Post Rail Kits | 9355
Bundle | P91-10KTB1 | Xtreme Power P91- 10KVA/10KW online double conversion UPS in 6U total rack/tower configuration; 208/240VAC input and 208/104V or 240/120V output; Bypass distribution module, 6kVA isolation transformer, 3U battery pack providing hot swappable battery trays and 2 minutes runtime at 10KW load; hardwire terminal block input; output (1) L6-30R, (2) L6-20R and (12) 5-15/20R receptacles (6KW max 120V capability); LCD display; intelligent slot for optional cards; RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 320 lbs. Package Includes: P91-10k UPS Power Module (2U), BPXR2U240A Battery Module (2U), XBDM-P91B Bypass PDU (0U) (2) C91 - L6-20R XPD-IT60A Isolation Transformer (2U), Tower Stands, Software; (3) 4 Post Rail Kits | 8901
Bundle | P91-10KTB2 | Xtreme Power P91- 10KVA/10KW online double conversion UPS in 8U total rack/tower configuration; 208/240VAC input and 208/104V or 240/120V output; Bypass distribution module, 10kW isolation transformer, 3U battery pack providing hot swappable battery trays and 6 minutes runtime at 10KW load; hardwire terminal block input; output terminal block and (1) L6-30R, (2) L14-30R and (8) 5-15/20R receptacles; LCD display; intelligent slot for optional cards; RS-232 and USB; Software; UL, cUL, FCC, RoHS; TAA Compliant; 3 year UPS and battery warranty (USA and Canada). Max Rack Depth 32.4"; Total Wt 49 lbs. Package Includes: P91-10k UPS Power Module (2U), BPXR3U240A Battery Module (3U), XBDM-P91C Bypass PDU (0U) XPD-IT10KW Isolation Transformer (3U), Tower Stands, Software; (3) 4 Post Rail Kits | 10187
P91 SERIES 5, 6 & 10KVA 208/230V Solutions
Part Number | MODEL | DESCRIPTION | LIST PRICE
90000640 | P91-5K | Xtreme Power P91 Series 5KVA/5kW Unity PF; Online UPS; 2U; 208VAC (selectable to 208, 220, 230 or 240); Input and Output connections are Terminal Block ; Set up for external batteries; adjustable 1-4 Amp 240V charger; Tower and rack mounting; 99% efficiency in ECO mode, Smart LCD screen; intelligent slot for optional cards, RS-232 and USB port connections; UL, cUL, FCC, RoHS approved; TAA Compliant; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 23.6"D x 3.5"H; 33.1 lbs. | 2310
90000641 | P91-6K | Xtreme Power P91 Series 6KVA/6kW Unity PF; Online UPS; 2U; 208VAC (selectable to 208, 220, 230 or 240); Input and Output connections are Terminal Block; Set up for external batteries; adjustable 1-4 Amp 240V charger; Tower and rack mounting; 99% efficiency in ECO mode, Smart LCD screen; intelligent slot for optional cards, RS-232 and USB port connections; UL, cUL, FCC, RoHS approved; TAA Compliant; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 23.6"D x 3.5"H; 34 lbs. | 2700
90000642 | P91-10K | Xtreme Power P91 Series 10KVA/10kW Unity PF; Online UPS; 2U; 208VAC (selectable to 208, 220, 230 or 240); Input and Output connections are Terminal Block; Set up for external batteries; adjusable 1-4 Amp 240V charger; Tower and rack mounting; 99% efficiency in ECO mode, intelligent slot for optional cards, Smart LCD screen; RS-232 and USB port connections; UL, cUL, FCC, RoHS approved; TAA Compliant; 3 year full Warranty (USA and Canada); 50K load protection policy; 17.2"W x 23.6"D x 3.5"H; 39.7 lbs. | 3780
90000643 | BPXR2U240A | Extended Runtime Battery Pack for use with P91- 5, 6 &10K UPSs; 2U; (includes 20 each 12V5AH batteries); Hot swappable internal battery trays; __ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower or Rack Mounting; Includes BP to UPS interconnection cable. TUV/UL, FCC, RoHS, cUL Approved; 3-Year Full Warranty (USA and Canada); 17.2"W x 27.4"D x 3.5"H; 120 lbs | 2050
90000644 | BPXR3U240A | Extended Runtime Battery Pack for use with P91-5, 6 &10K UPSs; 3U; (includes 20 each 12V580W batteries); Hot swappable internal battery trays; __ Battery Packs provide(s) __ minutes runtime @ __KVA load. Tower or Rack Mounting; Includes BP to UPS interconnection cable. TUV/UL, FCC, RoHS, cUL Approved; 3-Year Full Warranty (USA and Canada); 17.2"W x 27.4"D x 5.2"H; 160 lbs | 2470
90000645 | XBDM-P91A | XBDM, (Xtreme Bypass Distribution Module) for use with P91-5 & 6K UPSs; Input is L6-30P 6ft line cord; Outputs are (2) L6-30R and (2) C19 receptacles, breaker protected; Interconnection to and from UPS is via Anderson Connection cables and Cable for UPS static switch interlock(included). Includes Maintenance Bypass Switch; 0U, mounts to rear of battery pack or in rear of rack cabinet. 14.6"W x 5"D x 3.5"H. 8 lbs. | 730
| XBDM-P91A10 | XBDM, (Xtreme Bypass Distribution Module) for use with P91-5 & 6K UPSs; Input is L6-30P 10ft line cord; Outputs are (2) L6-30R and (2) C19 receptacles, breaker protected; Interconnection to and from UPS is via Anderson Connection cables and Cable for UPS static switch interlock(included). Includes Maintenance Bypass Switch; 0U, mounts to rear of battery pack or in rear of rack cabinet. 14.6"W x 5"D x 3.5"H. 8 lbs. | 760
90000646 | XBDM-P91B | XBDM, (Xtreme Bypass Distribution Module) for use with P91-5, 6 & 10K UPSs; Input is Terminal Block; Output is Terminal Block plus (1) L6-30R and (2) C19 receptacles, breaker protected; Interconnection to and from UPS is via Anderson Connection cables and Cable for UPS static switch interlock (included). Includes Maintenance Bypass Switch; 0U, mounts to rear of battery pack or in rear of rack cabinet; 14.6"W x 5"D x 3.5"H. 6 lbs. | 730
90000737 | XBDM-P91C | XBDM, (Xtreme Bypass Distribution Module) for use with P91-5, 6 & 10K UPSs; Input is Terminal Block; Output is Terminal Block plus (1) L6-30R, breaker protected; Interconnection to and from UPS is via Anderson Connection cables and Cable for UPS static switch interlock (included). Includes Maintenance Bypass Switch; 0U, mounts to rear of battery pack or in rear of rack cabinet. 14.6"W x 5"D x 3.5"H. 5lbs. | 730
90000738 | XBDM-P91D | XBDM, (Xtreme Bypass Distribution Module) for use with P91-5, 6 & 10K UPSs; Input is Terminal Block; Output is (2) L6-30R receptacles, breaker protected; Interconnection to and from UPS is via Anderson Connection cables and Cable for UPS static switch interlock(included). Includes Maintenance Bypass Switch; 0U, mounts to rear of battery pack or in rear of rack cabinet. 14.6"W x 5"D x 3.5"H. 6 lbs. | 730
| XPC-ZLC20-620R | Output Cord, 1ft, IEC Locking C20 to 6-15/20R for use with Xtreme Bypass Distribution Modules (XBDM) with C19 output. 1 lbs. | 79
| XPC-ZLC20-L620R | Output Cord,1ft, IEC Locking C20 to L6-20R for use with Xtreme Bypass Distribution Modules (XBDM) with C19 output. 1 lbs. | 79
| XPC-ZLC20-L630R | Output Cord, 1ft, IEC Locking C20 to L6-30R for use with Xtreme Bypass Distribution Modules (XBDM) with C19 output. 1 lbs. | 79
| XPC-C20-L615R | Output Cord, 1ft, IEC Non-locking C20 to L6-15R for use with Xtreme Bypass Distribution Modules (XBDM) with C19 output. 1 lbs. | 59
TBD | XPC-L630R | Optional L6-30R, 8" dongle style output receptacle for use with UPS with terminal block output; 12 lbs. | 125
TBD | XPC-L630P | Optional L6-30P line cord, 6ft line cord for use with 5 or 6K UPS with terminal block input; 12 lbs. | 125
90000407 | XPD-IT60A | Xtreme Power XPDU Series 6KVA PDU with Isolation Transformer for use with P80G-5000 or P91 5-10K UPS. 6000W, 208 or 240 in, 208/104V or 240/120V out. 3ft L6-30P Input Cord. (1) L6-30R and (12) 5-15-20R output receptacles; rear panel 208/240 voltage selection switch; includes front panel rackmount brackets; ROHS Approved; 3-Year Warranty; 17.3"W x 18"D x 3.5"H (2U), 137 lbs. | 1750
90000781 | XPD-IT6KW | 6kVA PDU with Isolation Transformer 208V to 240/120V (or 240V to 240/120V), Input terminal bock, Output terminal block + (2) L14-30R and (8) 5–15/20R receptacles; 17.3”W x 32.8”D x 5.2”H; 199 lbs. | 2310
90000740 | XPD-IT10KW | 10kVA PDU with Isolation Transformer 208V to 240/120V (or 240V to 240/120V), Input terminal bock, Output terminal block + (2) L14-30R and (8) 5–15/20R receptacles; 17.3”W x 32.8”D x 5.2”H; 209 lbs. | 2760
90000933 | P90L-RAIL | Adjustable Mounting 4-Post Rail Kit for P91 or P90L-5K, 6K, &10K UPS, BP & Transformer Module; extends from 21" to 35.5"; packaging = 3..8"W x 22"D x 2.8"H, 5 lbs | 149
90000116 | XPC-2POSTL | 2-Post Shelf Kit for P91 or P90L-5K, 6K, &10K UPS, BP & Transformer Module rated for 150lbs; 21/5"W x 23.3"D x 3.5"H. 9 lbs | 160
90003042 | XPC-2POST | Heavy Duty 2-Post Shelf Kit for P91 or P90L-5K, 6K, &10K UPS, BP & Transformer Module rated for 300lbs; 19"W x 29"D x 5.2"H. 14 lbs | 270
90000741 | SNMP-2PV3 | Internal SNMP/WEB Card for use with P80 or P90 Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-EMPV2 Environmental Monitor; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 359
90000674 | SNMP-EMPV2 | Environmental Monitoring Sensor to monitor room temperature and humidity - used with SNMP-2PV3 SNMP/WEB Card. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 230
90000267 | MODBUS-IN | MODBUS CARD for use with the P90L Series UPS; packaging = 7.25" x 6" x 2.5", 1 lbs | 319
90000265 | RELAY-MINI | Dry Contact RELAY CARD with DB9 & terminal block adapter; packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 120
90000374 | XPD24C13V | Xtreme Power XPDU Series Basic Power PDU, 30A, 200-240V; L6-30P 6ft line cord, (24) C13 output receptacles. Vertical Mount. 1.75"W x 1.75"D x 66"L. 12 lbs | 340
9000251 | XPD31 | Xtreme Power XPDU Series Basic Power PDU, 30A, 200-240V; L6-30P 6ft line cord, (2) L6-30R, (2) L6-20R and (4) 6-15/20R output receptacles. Rackmount. 19"W x 4.7"D x 3.5"H. 9 lbs | 580
90000252 | XPD32 | Xtreme Power XPDU Series Basic Power PDU, 30A, 200-240V; L6-30P 6ft line cord, (2) L6-30R, (4) L6-20R output receptacles. Rackmount. 19"W x 2.4"D x 3.5"H. 7.5 lbs | 580
90000253 | XPD33 | Xtreme Power XPDU Series Basic Power PDU, 30A, 200-240V; L6-30P 6ft line cord, (4) IEC-C19 and (8) IEC C13 output receptacle. s Rackmount. 19"W x 2.4"D x 3.5"H. 8 lbs | 450
90000254 | XPD34 | Xtreme Power XPDU Series Basic Power PDU, 30A, 240/120V; L14-30P 6ft line cord, (2) L6-30R, (4) L6-20R and (12) 5-20R output receptacles. Rackmount. 19"W x 4.7"D x 3.5"H. 9.5 lbs | 690
90000255 | XPD35 | Xtreme Power XPDU Series Basic Power PDU, 50A, 200-240V; Hardwire input with Pigtail, (2) L6-30R and (4) L6-20R output receptacles. Rackmount. 19"W x 2.4"D x 3.5"H. 7 lbs | 580
90000256 | XPD36 | Xtreme Power XPDU Series Basic Power PDU, 50A, 200-240V; Hardwired input with Pigtail, (4) IEC-C19 and (8) IEC C13 output receptacles. Rackmount. 19"W x 2.4"D x 3.5"H. 6.8 lbs | 460
P91 SERIES 5, 6 & 10KVA Service Plans
Part Number | MODEL | DESCRIPTION | LIST PRICE
90001282 | 9SUS8051 | P91 5x8 Startup and 1 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 3900
90001283 | 9SUS8052 | P91 5x8 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 4500
90001284 | 9USUS8053 | P91 5x8 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5100
90001285 | 9SU724051 | P91 7x24 Startup and 1 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5070
90001286 | 9SU724052 | P91 7x24 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5850
90001287 | 9SU724053 | P91 7x24 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioningof UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 6630
90000350 | P95P610 | Extended 5 Year Factory Warranty for P91-5K, P91-6K, and P91-10K | 1500
90001288 | 9PM58 | P91 Preventative Maintenance Service, 5x8. For Zone 1 (within 100 miles of XPC Service Center). | 3500
90001289 | 9PM724 | P91 Preventative Maintenance Service, 7x24. For Zone 1 (within 100 miles of XPC Service Center). | 4550
90000538 | SVCADD | Service adder for locations further than 100 miles. | 1050
90000355 | P9OS3BP | On-Site 3 Year service plan for BPXR2U240A and BPXR3U240A battery packs | 480
90000356 | P9OS5BP | On-Site 5 Year service plan for BPXR2U240A and BPXR3U240A battery packs | 1140
90000946 | P90L5SPBP2 | Extended 5 Year Factory Warranty for BPXR2U240A and BPXR3U240A battery packs | 700

## TX91(L) 3.8 - 10K
2024-08-01
TX91 Series Isolated Online UPS
TX91 3.8kVA UPS
90000579 | TX91-3.8K | Xtreme Power TX91 Series 3.8kVA/3.8kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; Full Load Runtime = 15 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 272 lbs. | 6350
90000572 | TX91-3.8KXR | Xtreme Power TX91 Series 3.8kVA/3.8kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; 580W batteries for Full Load Runtime = 21 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 275 lbs. | 8050
| TX91-3.8KB1#### | Xtreme Power TX91 Series 3.8kVA/3.8kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (6) Configurable 240V and (4) 5-15/20R output connections; (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Full Load Runtime = 15 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 277 lbs. | 7540
| TX91-3.8KXRB1#### | Xtreme Power TX91 Series 3.8kVA/3.8kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (6) Configurable 240V and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; 580W batteries for Full Load Runtime = 21 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 280 lbs. | 9240
| TX91-3.8KB2#### | Xtreme Power TX91 Series 3.8kVA/3.8kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (4) Configurable 240V, (1) L6-30R, and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Full Load Runtime = 15 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 277 lbs. | 7540
| TX91-3.8KXRB2#### | Xtreme Power TX91 Series 3.8kVA/3.8kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (4) Configurable 240V, (1) L6-30R, and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; 580W batteries for Full Load Runtime = 21 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 280 lbs. | 9240
90000587 | TX91L-3.8K | Xtreme Power TX91L Series 3.8kVA/3.8kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; Set up for external batteries; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 152 lbs. External batteries to be ordered seperately. | 5100
| TX91L-3.8KB1#### | Xtreme Power TX91L Series 3.8kVA/3.8kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (6) Configurable 240V and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R. D = (1) L6-15R; Set up for external batteries; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 157 lbs. External batteries to be ordered seperately. | 6290
| TX91L-3.8KB2#### | Xtreme Power TX91L Series 3.8kVA/3.8kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (4) Configurable 240V, (1) L6-30R, and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Set up for external batteries; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 157 lbs. External batteries to be ordered seperately. | 6290
TX91 5kVA UPS
90000573 | TX91-5K | Xtreme Power TX91 Series 5kVA/5kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; Full Load Runtime = 10 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 275 lbs. | 7200
90000574 | TX91-5KXR | Xtreme Power TX91 Series 5kVA/5kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; 580W batteries for Full Load Runtime = 15 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 278 lbs. | 8900
| TX91-5KB1#### | Xtreme Power TX91 Series 5kVA/5kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (6) Configurable 240V and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Full Load Runtime = 10 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 280 lbs. | 8390
| TX91-5KXRB1#### | Xtreme Power TX91 Series 5kVA/5kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (6) Configurable 240V and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; 580W batteries for Full Load Runtime = 15 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 283 lbs. | 10090
| TX91-5KB2#### | Xtreme Power TX91 Series 5kVA/5kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (4) Configurable 240V, (1) L6-30R and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Full Load Runtime = 10 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 280 lbs. | 8390
| TX91-5KXRB2#### | Xtreme Power TX91 Series 5kVA/5kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (4) Configurable 240V, (1) L6-30R and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; 580W batteries for Full Load Runtime = 15 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 283 lbs. | 10090
90000588 | TX91L-5K | Xtreme Power TX91L Series 5kVA/5kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; Set up for external batteries; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 155 lbs. External batteries to be ordered seperately. | 6050
| TX91L-5KB1#### | Xtreme Power TX91L Series 5kVA/5kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (6) Configurable 240V and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Set up for external batteries; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 160 lbs. External batteries to be ordered seperately. | 7240
| TX91L-5KB2#### | Xtreme Power TX91L Series 5kVA/5kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (4) Configurable 240V, (1) L6-30R and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Set up for external batteries; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 160 lbs. External batteries to be ordered seperately. | 7240
TX91 6kVA UPS
90000575 | TX91-6K | Xtreme Power TX91 Series 6kVA/6kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; Full Load Runtime = 8 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 278 lbs. | 8050
90000576 | TX91-6KXR | Xtreme Power TX91 Series 6kVA/6kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; 580W batteries for Full Load Runtime = 12 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 281 lbs. | 9750
| TX91-6KB1#### | Xtreme Power TX91 Series 6kVA/6kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (6) Configurable 240V and (4) 5-15/20R output connections; (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Full Load Runtime = 8 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 283 lbs. | 9240
| TX91-6KXRB1#### | Xtreme Power TX91 Series 6kVA/6kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (6) Configurable 240V and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; 580W batteries for Full Load Runtime = 12 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 286 lbs. | 10940
| TX91-6KB2#### | Xtreme Power TX91 Series 6kVA/6kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (4) Configurable 240V, (1) L6-30R, and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Full Load Runtime = 8 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 277 lbs. | 9240
| TX91-6KXRB2#### | Xtreme Power TX91 Series 6kVA/6kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (4) Configurable 240V, (1) L6-30R, and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; 580W batteries for Full Load Runtime = 12 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 286 lbs. | 10940
90000589 | TX91L-6K | Xtreme Power TX91L Series 6kVA/6kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; Set up for external batteries; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 158 lbs. External batteries to be ordered seperately. | 6800
| TX91L-6KB1#### | Xtreme Power TX91L Series 6kVA/6kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (6) Configurable 240V and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Set up for external batteries; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 163 lbs. External batteries to be ordered seperately. | 7990
| TX91L-6KB2#### | Xtreme Power TX91L Series 6kVA/6kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (4) Configurable 240V, (1) L6-30R, and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Set up for external batteries; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 163 lbs. External batteries to be ordered seperately. | 7990
TX91 10kVA UPS
90000577 | TX91-10K | Xtreme Power TX91 Series 10kVA/10kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; Full Load Runtime = 3 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 307 lbs. | 11340
90000574 | TX91-10KXR | Xtreme Power TX91 Series 10kVA/10kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; 580W batteries for Full Load Runtime = 6 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; 3-Year Electronics, TAA Compliant; 3-Year Battery Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 310 lbs. | 12900
| TX91-10KB1#### | Xtreme Power TX91 Series 10kVA/10kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and (6) Configurable 240V and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Full Load Runtime = 3 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 312 lbs. | 12530
| TX91-10KXRB1#### | Xtreme Power TX91 Series 10kVA/10kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and (6) Configurable 240V and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; 580W batteries for Full Load Runtime = 6 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 315 lbs. | 14090
| TX91-10KB2#### | Xtreme Power TX91 Series 10kVA/10kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and (4) Configurable 240V, (1) L6-30R and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Full Load Runtime = 3 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 312 lbs. | 12530
| TX91-10KXRB2#### | Xtreme Power TX91 Series 10kVA/10kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and (4) Configurable 240V, (1) L6-30R and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; 580W batteries for Full Load Runtime = 6 minutes; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics, 3-Year Battery Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 315 lbs. | 14090
90000588 | TX91L-10K | Xtreme Power TX91L Series 10kVA/10kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; Set up for external batteries; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 187 lbs. External batteries to be ordered seperately. | 9240
| TX91L-10KB1#### | Xtreme Power TX91L Series 10kVA/10kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and (6) Configurable 240V and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Set up for external batteries; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 192 lbs. External batteries to be ordered seperately. | 10430
| TX91L-10KB2#### | Xtreme Power TX91L Series 10kVA/10kW Isolated Online UPS, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and (4) Configurable 240V, (1) L6-30R and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Set up for external batteries; ECO mode; Isolation transformer; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 192 lbs. External batteries to be ordered seperately. | 10430
TX91 Battery Options
Part Number | Model | Description | List Price
90000584 | TX91-BP960-1 | External Battery Pack Module for TX91 3.8 - 10kVA UPS, Contains 1 String of batteries (20), Up to three battery packs per UPS can be used for extended runtime applications; __ Battery Packs provide(s) __ minutes runtime @ __KVA load., 9.8"W x 22.3"D x 32.4"H, 190 lbs | 3400
90000585 | TX91-BP960-2 | External Battery Pack Module for TX91 3.8 - 10kVA UPS, Contains 2 Strings of batteries (40), Up to three battery packs per UPS can be used for extended runtime applications; __ Battery Packs provide(s) __ minutes runtime @ __KVA load., 9.8"W x 22.3"D x 32.4"H, 320 lbs | 4900
90000586 | TX91-BP960-3 | External Battery Pack Module for TX91 3.8 - 10kVA UPS, Contains 3 Strings of batteries (60), Up to three battery packs per UPS can be used for extended runtime applications; __ Battery Packs provide(s) __ minutes runtime @ __KVA load., 9.8"W x 22.3"D x 32.4"H, 450 lbs | 6450
90000762 | TX91-CHG | TX91 External Battery Charger. Rated at 240VDC, 8A output with output cable to plug into TX91-BP960-x battery pack. Input rated at 208-240 VAC, 10A hardwired input. | 780
TX91 External Bypass Switch Options
| 90885-C241310ECA050A05013MB | Three-Breaker Maintenance Bypass Switch; 240VAC, Single-Phase, 50 A, 10kAIC; rated for up to 8KVA; Wallmount; includes UPS Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker,interlock plate, lockable front panel, UL981, Black. 22"W x 24"H x 9"D; 55 lbs. | Call for Price
| 90885-C241310ECA070A07013MB | Three-Breaker Maintenance Bypass Switch; 240VAC, Single-Phase, 70 A, 10kAIC; rated for up to 12KVA; Wallmount; includes UPS Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker,interlock plate, lockable front panel, UL981, Black. 22"W x 24"H x 9"D; 55 lbs. | Call for Price
TX91 Output Cords
Part Number | Model | Description | List Price
| XPC-ZLC20-620R | Optional 12" output cord, Locking C20 to 6-15/20 receptacle for use with TX91; 3 lbs. | 79
| XPC-ZLC20-L620R | Optional 12" output cord, Locking C20 to L6-20 receptacle for use with TX91; 3 lbs. | 79
| XPC-ZLC20-L630R | Optional 12" output cord, Locking C20 to L6-30 receptacle for use with TX91; 3 lbs. | 79
| XPC-C20-L615R | Optional 12" output cord. Non-locking C20 to L6-15 receptacle for use with TX91; 3 lbs | 59
TBD | XPC-L630R | Optional L6-30R, 8" dongle style output receptacle for use with UPS with terminal block output; 12 lbs. | 125
TBD | XPC-L630P | Optional L6-30P line cord, 6ft line cord for use with 5 or 6K UPS with terminal block input; 12 lbs. | 125
TBD | XPC-L1430R | Optional L14-30R, 8" dongle style output receptacle for use with TX90-6K; 12 lbs. | 125
TX91 Distribution Options
Part Number | Model | Description | List Price
90000251 | XPD31 | Xtreme Power XPDU Series Basic Power PDU for use with TX91-3.8KVA - 10KVA UPS, 30A, 200-240V; L6-30P 6ft line cord, (2) L6-30R, (2) L6-20R and (4) 6-15/20R output receptacles. Rackmount. 19"W x 4.7"D x 3.5"H. 9 lbs | 580
90000252 | XPD32 | Xtreme Power XPDU Series Basic Power PDU for use with TX91-3.8KVA - 10KVA UPS, 30A, 200-240V; L6-30P 6ft line cord, (2) L6-30R, (4) L6-20R output receptacles. Rackmount. 19"W x 2.4"D x 3.5"H. 7.5 lbs | 580
90000253 | XPD33 | Xtreme Power XPDU Series Basic Power PDU for use with TX91-3.8KVA - 10KVA UPS, 30A, 200-240V; L6-30P 6ft line cord, (4) IEC-C19 and (8) IEC C13 output receptacle. s Rackmount. 19"W x 2.4"D x 3.5"H. 8 lbs | 450
90000254 | XPD34 | Xtreme Power XPDU Series Basic Power PDU, 30A, 240/120V; L14-30P 6ft line cord, (2) L6-30R, (4) L6-20R and (12) 5-20R output receptacles. Rackmount. 19"W x 4.7"D x 3.5"H. 9.5 lbs | 690
90001037 | XPD38 | Xtreme Power XPDU Series Basic Power PDU, 30A, 120V; L14-30P, 6' input cord , (4) L5-30R, (4) L5-20R output receptacles. Rackmount. 19"W x 4.7"D x 3.5"H. 9.5 lbs | 690
TX91 Communication Options
Part Number | Model | Description | List Price
90000741 | SNMP-2PV3 | Internal SNMP/WEB Card for use with TX91 Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-EMPV2 Environmental Monitor; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 359
90000674 | SNMP-EMPV2 | Environmental Monitoring Sensor to monitor room temperature and humidity - used with SNMP-2PV3 SNMP/WEB Card. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 230
90000267 | MODBUS-IN | MODBUS CARD for use with the TX91 Series UPS; packaging = 7.25" x 6" x 2.5", 1 lbs | 319
90000265 | RELAY-MINI | Dry Contact RELAY CARD with DB9 & terminal block adapter; packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 120
TX91 Warranty and Service Options
Part Number | Model | Description | List Price
90001282 | 9SUS8051 | M90S 5x8 Startup and 1 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 3900
90001283 | 9SUS8052 | M90S 5x8 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 4500
90001284 | 9USUS8053 | M90S 5x8 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5100
90001285 | 9SU724051 | M90S 7x24 Startup and 1 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5070
90001286 | 9SU724052 | M90S 7x24 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5850
90001287 | 9SU724053 | M90S 7x24 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioningof UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 6630
90001288 | 9PM58 | M90S Preventative Maintenance Service, 5x8. For Zone 1 (within 100 miles of XPC Service Center). | 3500
90001289 | 9PM724 | M90S Preventative Maintenance Service, 7x24. For Zone 1 (within 100 miles of XPC Service Center). | 4550
90000538 | SVCADD | Service adder for locations further than 100 miles. | 1050
90000375 | T9VCNFG | Non-Standard Voltage Configuration adder. Required when setting the TX91 (XR), TX91L, or TXVR input voltage to 200V, 230V, or 240V. Input Voltage: Output Voltage on-line/inverter: Output Voltage on Bypass: Displayed Voltage: | 300

## TXVR
|  | Return to Index | August 1. 2024
TXVR Voltage Regulator 3.8kVA - 10kVA
Part Number | Model | Description | List Price
90000494 | TXVR-3.8K | Xtreme Power TXVR Series 3.8kVA/3.8kW Isolated Electronic Voltage Regulator, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; Isolation transformer; regulates voltage to within +/- 1%; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL, cUL, RoHS Listed; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 142 lbs. | 4260
| TXVR-3.8KB1#### | Xtreme Power TXVR Series 3.8kVA/3.8kW Isolated Electronic Voltage Regulator, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (6) Configurable 240V and (4) 5-15/20R output connections; (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Isolation transformer; regulates voltage to within +/- 1%; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 147 lbs. | 5810
| TXVR-3.8KB2#### | Xtreme Power TXVR Series 3.8kVA/3.8kW Isolated Electronic Voltage Regulator, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (4) Configurable 240V, (1) L6-30R, and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Isolation transformer; regulates voltage to within +/- 1%; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 147 lbs. | 5810
TXVR 5kVA Voltage Regulator
90000495 | TXVR-5K | Xtreme Power TXVR Series 5kVA/5kW Isolated Electronic Voltage Regulator, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; Isolation transformer; regulates voltage to within +/- 1%; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 145 lbs. | 5900
| TXVR-5KB1#### | Xtreme Power TXVR Series 5kVA/5kW Isolated Electronic Voltage Regulator, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (6) Configurable 240V and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Isolation transformer; regulates voltage to within +/- 1%; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 150 lbs. | 7090
| TXVR-5KB2#### | Xtreme Power TXVR Series 5kVA/5kW Isolated Electronic Voltage Regulator, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (4) Configurable 240V, (1) L6-30R and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Isolation transformer; regulates voltage to within +/- 1%; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 150 lbs. | 7090
TXVR 6kVA Voltage Regulator
90000496 | TXVR-6K | Xtreme Power TXVR Series 6kVA/6kW Isolated Electronic Voltage Regulator, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; Isolation transformer; regulates voltage to within +/- 1%; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 148 lbs. | 6250
| TXVR-6KB1#### | Xtreme Power TXVR Series 6kVA/6kW Isolated Electronic Voltage Regulator, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (6) Configurable 240V and (4) 5-15/20R output connections; (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Isolation transformer; regulates voltage to within +/- 1%; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 153 lbs. | 7440
| TXVR-6KB2#### | Xtreme Power TXVR Series 6kVA/6kW Isolated Electronic Voltage Regulator, 208V input voltage; 240/120Vor 208V output voltage; 6 ft L6-30P input and (4) Configurable 240V, (1) L6-30R, and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Isolation transformer; regulates voltage to within +/- 1%; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 153 lbs. | 7440
TXVR 10kVA Voltage Regulator
90000497 | TXVR-10K | Xtreme Power TXVR Series 10kVA/10kW Isolated Electronic Voltage Regulator, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and output power connection; Isolation transformer; regulates voltage to within +/- 1%; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 23.2"D x 32.4"H, 187 lbs. | 8710
| TXVR-10KB1#### | Xtreme Power TXVR Series 10kVA/10kW Isolated Electronic Voltage Regulator, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and (6) Configurable 240V and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Isolation transformer; regulates voltage to within +/- 1%; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 192 lbs. | 9905
| TXVR10KB2#### | Xtreme Power TXVR Series 10kVA/10kW Isolated Electronic Voltage Regulator, 208V input voltage; 240/120Vor 208V output voltage; Terminal block input and (4) Configurable 240V, (1) L6-30R and (4) 5-15/20R output connections (choose four, and replace the ## in the P/N) A = (1) L6-20R, B = (1) L6-30R, C = (1) 6-15/20R, D = (1) L6-15R; Isolation transformer; regulates voltage to within +/- 1%; Tower; internal maintenance bypass; lockable casters; RS232, USB, Intelligent Ports, EPO Port: Communications Cable and Shutdown Software; UL1778, cUL, FCC Class A, RoHS Listed.; TAA Compliant; 3-Year Electronics Warranty (USA and Canada); 9.8"W x 27.1"D x 32.4"H, 192 lbs. | 9905
TX91 Output Cords
Part Number | Model | Description | List Price
| XPC-ZLC20-620R | Optional 12" output cord, Locking C20 to 6-15/20 receptacle for use with TXVR; 3 lbs. | 79
| XPC-ZLC20-L620R | Optional 12" output cord, Locking C20 to L6-20 receptacle for use with TXVR; 3 lbs. | 79
| XPC-ZLC20-L630R | Optional 12" output cord, Locking C20 to L6-30 receptacle for use with TXVR; 3 lbs. | 79
| XPC-C20-L615R | Optional 12" output cord. Non-locking C20 to L6-15 receptacle for use with TX91; 3 lbs | 59
TBD | XPC-L630P | Optional L6-30P line cord, 6ft line cord for use with T90-6K or TX90-6K; 12 lbs. | 125
TBD | XPC-L630R | Optional L6-30R, 8" dongle style output receptacle for use with T90-6K or TX90-6K; 12 lbs. | 125
TBD | XPC-L1430R | Optional L14-30R, 8" dongle style output receptacle for use with TX90-6K; 12 lbs. | 125
TX91 Distribution Options
Part Number | Model | Description | List Price
90000251 | XPD31 | Xtreme Power XPDU Series Basic Power PDU for use with TXVR Series, 30A, 200-240V; L6-30P 6ft line cord, (2) L6-30R, (2) L6-20R and (4) 6-15/20R output receptacles. Rackmount. 19"W x 4.7"D x 3.5"H. 9 lbs | 580
90000252 | XPD32 | Xtreme Power XPDU Series Basic Power PDU for use with TXVR Series, 30A, 200-240V; L6-30P 6ft line cord, (2) L6-30R, (4) L6-20R output receptacles. Rackmount. 19"W x 2.4"D x 3.5"H. 7.5 lbs | 580
90000253 | XPD33 | Xtreme Power XPDU Series Basic Power PDU for use with TXVR Series, 30A, 200-240V; L6-30P 6ft line cord, (4) IEC-C19 and (8) IEC C13 output receptacle. s Rackmount. 19"W x 2.4"D x 3.5"H. 8 lbs | 450
90000254 | XPD34 | Xtreme Power XPDU Series Basic Power PDU, 30A, 240/120V; L14-30P 6ft line cord, (2) L6-30R, (4) L6-20R and (12) 5-20R output receptacles. Rackmount. 19"W x 4.7"D x 3.5"H. 9.5 lbs | 690
90001037 | XPD38 | Xtreme Power XPDU Series Basic Power PDU, 30A, 120V; L14-30P, 6' input cord , (4) L5-30R, (4) L5-20R output receptacles. Rackmount. 19"W x 4.7"D x 3.5"H. 9.5 lbs | 690
TX91 Communication Options
Part Number | Model | Description | List Price
90000741 | SNMP-2PV3 | Internal SNMP/WEB Card for use with TXVR Series; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-EMPV2 Environmental Monitor; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 359
90000674 | SNMP-EMPV2 | Environmental Monitoring Sensor to monitor room temperature and humidity - Must be used with SNMP-2PV3 SNMP/WEB Card. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 230
90000267 | MODBUS-IN | MODBUS CARD for use with the TXVR Series UPS; packaging = 7.25" x 6" x 2.5", 1 lbs | 319
90000265 | RELAY-MINI | Dry Contact RELAY CARD with DB9 & terminal block adapter; packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 120
TX91 Warranty and Service Options
Part Number | Model | Description | List Price
90001282 | 9SUS8051 | M90S 5x8 Startup and 1 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 3900
90001283 | 9SUS8052 | M90S 5x8 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 4500
90001284 | 9USUS8053 | M90S 5x8 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5100
90001285 | 9SU724051 | M90S 7x24 Startup and 1 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5070
90001286 | 9SU724052 | M90S 7x24 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5850
90001287 | 9SU724053 | M90S 7x24 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioningof UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 6630
90001288 | 9PM58 | M90S Preventative Maintenance Service, 5x8. For Zone 1 (within 100 miles of XPC Service Center). | 3500
90001289 | 9PM724 | M90S Preventative Maintenance Service, 7x24. For Zone 1 (within 100 miles of XPC Service Center). | 4550
90000538 | SVCADD | Service adder for locations further than 100 miles. | 1050
90000375 | T9VCNFG | Non-Standard Voltage Configuration adder. Required when setting the TX91 (XR), TX91L, or TXVR input voltage to 200V, 230V, or 240V. Input Voltage: Output Voltage on-line/inverter: Output Voltage on Bypass: Displayed Voltage: | 300

## M90S Modular Single Phase
|  | Return to Index | 2024-08-01
M90S Series Modular Double Conversion Split-Phase
M90S Series Ala Carte Solutions
Part Number | Model | Description | List Price
90000690 | M90S-ENC2 | XPC M90S 2-slot enclosure; Up to 6kVA/6kW; On Line - Rack Mount configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Integral Rear Mounted Maintenance Bypass switch, RS-232, USB, dry contacts, EPO, intelligent slot for optional card (Web/SNMP, Relay, Modbus); Communication Software and Cable; UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Power Module and Battery Module purchased separately; Unit Dims: 17.4"W X 33.7"D x 10.5"H. Weight: 38 lbs. | 1800
90000691 | M90S-ENC4 | XPC M90S 4-slot enclosure; Up to 12kVA/12kW; On Line - Tower configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Integral Front Access Maintenance Bypass switch, Floor mount bracket; Communications Module; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable; UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Power Modules, Battery Modules, and Blank Panels purchased separately; Dims: 17.4"W X 33.7"D x 33"H. Weight: 150 lbs. | 4800
90000692 | M90S-ENC6 | XPC M90S 6-slot enclosure; Up to 24kVA/24kW; On Line - Tower configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Integral Front Access Maintenance Bypass switch, Floor mount bracket; Communications Module; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus) Communication Software and Cable; UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Power Modules, Battery Modules, and Blank Panels purchased separately; Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 180 lbs. | 7250
90000693 | M90S-PWM6 | 6KVA/6KW Power Module for XPC M90S UPS; On Line- 120/208V In-120/208V Out or 120/240V In - 120/240V Out; LCD Screen, Dims: 16.3"W X 24"D x 5.2"H (3U). Weight: 38 lbs. | 4190
90001262 | M90S-BMXRV2 | Battery Module for XPC M90S UPS; Contains two battery sleeves, each containing (8) 12V 580W batteries; battery breaker; 16.3"W X 24"D x 5.2"H. Weight: 107 lbs. Note: Minimum of one battery module required for each power module used for capacity. | 2095
90000696 | M90S-BC7 | XPC M90S External Battery Enclosure; 7-slot enclosure holds up to (7) M90S-BMXR battery modules; Includes Casters. Battery Modules and Blank Panels purchased separately; Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 162 lbs. | 4935
90000717 | XPC-L14-30P | L14-30P input cord, 8 ft, (6KVA UPS only). Limits current to 24A continuous input current. | 135
90000719 | M90S-CB | Caster Base for M90S-ENC2. Locking casters. Dims: 17"W X 24"D x 4.0"H. Weight: 15 lbs. | 610
90000703 | M90S-BP | M90S Matching Blank Panel covers front of unused slots. Dims: 16.5"W X 2"D x 5.2"H. Weight: 5 lbs. | 63
90000695 | M90S-RAIL2S | M90S Rail Kit for M90S-ENC2 2-slot enclosure. Dims: 20"W X 4"D x 2.5"H. Weight: 5 lbs. | 155
90001332 | M90S-RMK | Rack mount kit to mount M90S-4S, M90S-6S, M90C-6S, M90Ci-6S, or M90S-BC7 enclosures into the bottom of a 19" rack. Includes: Ramp, Shelf, ann Front Mounting Ears | 680
| M90S4S-SEIS | Seismic Hold Down Achorage for M90S-ENC4 enclosure. Includes calculations with State of California Engineer Stamp. | 1900
| M90S6S-SEIS | Seismic Hold Down Achorage for M90S-ENC6 enclosure. Includes calculations with State of California Engineer Stamp. | 1900
M90S Series Optional Receptacle Panels (6S = up to 4 RP) (4S = up to 2 RP), (2S = up to 1 RP)
Part Number | Model | Description | List Price
90000699 | M90S-RPA | XPC M90S Optional Receptacle Panel. Contains (8) 5-20R receptacles. Mounts to rear of UPS Chassis. Weight: 5 lbs. | 295
90000700 | M90S-RPB | XPC M90S Optional Receptacle Panel. Contains (2) C19 and (4) 5-20R receptacles. Mounts to rear of UPS Chassis. Weight: 5 lbs. | 295
90000701 | M90S-RPC | XPC M90S Optional Receptacle Panel. Contains (1) L6-30R and (2) C19 receptacles. Mounts to rear of UPS Chassis. Weight: 5 lbs. | 295
90000703 | M90S-RPD | XPC M90S Optional Receptacle Panel. Contains (1) L14-30R and (2) C19 receptacles. Mounts to rear of UPS Chassis. Weight: 5 lbs. | 295
Bundle | M90S-RPE | XPC M90S Optional Receptacle Panel. Contains (2) L6-20R and (4) 5-20R receptacles. Mounts to rear of UPS Chassis. Weight: 5 lbs. | 453
Bundle | M90S-RPF | XPC M90S Optional Receptacle Panel. Contains (1) L6-30R, (1) L6-20R and (4) 5-20R receptacles. Mounts to rear of UPS Chassis. L6-30R protected by 20A breaker; Weight: 5 lbs. | 453
Bundle | M90S-RPG | XPC M90S Optional Receptacle Panel. Contains (1) L6-30R and (2) L6-20R receptacles. Mounts to rear of UPS Chassis. Weight: 5 lbs. | 453
Bundle | M90S-RPH | XPC M90S Optional Receptacle Panel. Contains (3) L6-30R receptacles. Mounts to rear of UPS Chassis. (2) L6-30R protected by 20A breakers; Weight: 5 lbs. | 453
M90S Series Hardwired Bundled Solutions
M90S 2-Slot 6KVA RM Hardwired Bundled Solutions
Part Number | Model | Description | List Price
Bundle | M90S-2S6K | XPC M90S UPS bundle; 6kVA/6kW; On Line-Rackmount Configuration,120/208V In/Out or 120/240V In/Out, Hardwired in/out. Bundle includes M90S-ENC2 2-Slot Enclosure with Integral Maintenance Bypass, Rackmount rails; (1) Power Module and (1) Battery Module providing 9 minutes runtime @ 6KVA/6KW load; RS-232, USB, dry contacts, EPO, intelligent slot for optional card (Web/SNMP, Relay, Modbus; ) Communication Software and Cable; UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 16.3"W X 24"D x 10.5"H. Weight: 185 lbs. | 8240
Bundle | M90S-2S6KT | XPC M90S UPS bundle; 6kVA/6kW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out. Bundle includes M90S-ENC2 2-Slot Enclosure with Integral Maintenance Bypass; Caster Base, (1) Power Module and (1) Battery Module providing 9 minutes runtime @ 6KVA/6KW load; RS-232, USB, dry contacts, EPO, intelligent slot for optional card (Web/SNMP, Relay, Modbus) Communication Software and Cable; UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, Battery Module and Caster Base shipped seperately. Dims: 17"W X 24"D x 14.5"H. Weight: 198 lbs. | 8695
M90S 4-Slot 6KVA Hardwired Bundled Solutions
Part Number | Model | Description | List Price
| M90S-4S6K1 | XPC M90S UPS bundle; 6KVA/6KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC4 4 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) Power Module, (1) Battery Module providing 9 minutes runtime @ 6KVA/6KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 33"H. Weight: 275 lbs. | 11211
| M90S-4S6K2 | XPC M90S UPS bundle; 6KVA/6KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC4 4 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) Power Module, (2) Battery Modules providing 22 minutes runtime @ 6KVA/6KW load, RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 33"H. Weight: 382 lbs. | 13243
| M90S-4S6K3 | XPC M90S UPS bundle; 6KVA/6KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC4 4 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) Power Module, (3) Battery Modules providing 35 minutes runtime @ 6KVA/6KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 33"H. Weight: 489 lbs. | 15275
M90S 4-Slot 12KVA Hardwired Bundled Solutions
Part Number | Model | Description | List Price
| M90S-4S12K2 | XPC M90S UPS bundle; 12KVA/12KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC4 4 Slot Enclosure with Integral Front Access Maintenance Bypass, (2) Power Modules, (2) Battery Modules providing 9 minutes runtime @ 12KVA/12KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 33"H. Weight: 420 lbs. | 17370
M90S 6-Slot 6KVA Hardwired Bundled Solutions
Part Number | Model | Description | List Price
| M90S-6S6K1 | XPC M90S UPS bundle; 6KVA/6KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) Power Module, (1) Battery Module providing 9 minutes runtime @ 6KVA/6KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 314 lbs. | 13787
| M90S-6S6K2 | XPC M90S UPS bundle; 6KVA/6KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) Power Module, (2) Battery Modules providing 22 minutes runtime @ 6KVA/6KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 421 lbs. | 15819
| M90S-6S6K3 | XPC M90S UPS bundle; 6KVA/6KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) Power Module, (3) Battery Modules providing 35 minutes runtime @ 6KVA/6KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 528 lbs. | 17851
| M90S-6S6K4 | XPC M90S UPS bundle; 6KVA/6KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) Power Module, (4) Battery Modules providing 50 minutes runtime @ 6KVA/6KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 635 lbs. | 19883
| M90S-6S6K5 | XPC M90S UPS bundle; 6KVA/6KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) Power Module, (5) Battery Modules providing 66 minutes runtime @ 6KVA/6KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 742 lbs. | 21915
M90S 6-Slot 12KVA Hardwired Bundled Solutions
Part Number | Model | Description | List Price
| M90S-6S12K2 | XPC M90S UPS bundle; 12KVA/12KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (2) Power Modules, (2) Battery Modules providing 9 minutes runtime @ 12KVA/12KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 459 lbs. | 19946
| M90S-6S12K3 | XPC M90S UPS bundle; 12KVA/12KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (2) Power Modules, (3) Battery Modules providing 15 minutes runtime @ 12KVA/12KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 566 lbs. | 21978
| M90S-6S12K4 | XPC M90S UPS bundle; 12KVA/12KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (2) Power Modules, (4) Battery Modules providing 22 minutes runtime @ 12KVA/12KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); , Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 673 lbs. | 24010
M90S 6-Slot 18KVA Hardwired Bundled Solutions
Part Number | Model | Description | List Price
| M90S-6S18K3 | XPC M90S UPS bundle; 18KVA/18KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (3) Power Modules, (3) Battery Modules providing 9 minutes runtime @ 18KVA/18KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 604 lbs. | 26105
M90S 6-Slot 24KVA Hardwired Bundled Solutions
Part Number | Model | Description | List Price
| M90S-6S24K4 | XPC M90S / BC7 UPS bundle; 24KVA/24KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (4) Power Modules, (2) Battery Modules,and M90S-BC7-2 Bundle providing 9 minutes runtime @ 24KVA/24KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 3 year UPS and battery warranty (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. UPS Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 535 lbs BC7 Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 376 lbs | 39798
M90S Battery Cabinet Bundles
Part Number | Model | Description | List Price
| M90S-BC7-1 | XPC M90S Battery Cabinet bundle; Includes XPC M90S-BC7 7 Slot External Battery Enclosure; (1) battery module; DC Breaker; Casters. 3 year battery warranty (USA and Canada). Increases runtime to __ minutes runtime @ __KVA/__KW load; Enclosure and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 269 lbs | 7408
| M90S-BC7-2 | XPC M90S Battery Cabinet bundle; Includes XPC M90S-BC7 7 Slot External Battery Enclosure; (2) battery modules; DC Breaker; Casters. 3 year battery warranty (USA and Canada). Increases runtime to __ minutes runtime @ __KVA/__KW load; Enclosure and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 376 lbs | 9440
| M90S-BC7-3 | XPC M90S Battery Cabinet bundle; Includes XPC M90S-BC7 7 Slot External Battery Enclosure; (3) battery modules; DC Breaker; Casters. 3 year battery warranty (USA and Canada). Increases runtime to __ minutes runtime @ __KVA/__KW load; Enclosure and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 483 lbs | 11472
| M90S-BC7-4 | XPC M90S Battery Cabinet bundle; Includes XPC M90S-BC7 7 Slot External Battery Enclosure; (4) battery modules; DC Breaker; Casters. 3 year battery warranty (USA and Canada). Increases runtime to __ minutes runtime @ __KVA/__KW load; Enclosure and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 590 lbs | 13504
| M90S-BC7-5 | XPC M90S Battery Cabinet bundle; Includes XPC M90S-BC7 7 Slot External Battery Enclosure; (5) battery modules; DC Breaker; Casters. 3 year battery warranty (USA and Canada). Increases runtime to __ minutes runtime @ __KVA/__KW load; Enclosure and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 697 lbs | 15536
| M90S-BC7-6 | XPC M90S Battery Cabinet bundle; Includes XPC M90S-BC7 7 Slot External Battery Enclosure; (6) battery modules; DC Breaker; Casters. 3 year battery warranty (USA and Canada). Increases runtime to __ minutes runtime @ __KVA/__KW load; Enclosure and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 804 lbs | 17568
| M90S-BC7-7 | XPC M90S Battery Cabinet bundle; Includes XPC M90S-BC7 7 Slot External Battery Enclosure; (7) battery modules; DC Breaker; Casters. 3 year battery warranty (USA and Canada). Increases runtime to __ minutes runtime @ __KVA/__KW load; Enclosure and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 911 lbs | 19600
M90S External Bypass Options
| 90885-C241310ECA050A05013MB | Three-Breaker Maintenance Bypass Switch; 240VAC, Single-Phase, 50 A, 10kAIC; rated for up to 8KVA; Wallmount; includes UPS Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker,interlock plate, lockable front panel, UL981, Black. 22"W x 24"H x 9"D; 55 lbs. | Call for Price
| 90885-C241310ECA070A07013MB | Three-Breaker Maintenance Bypass Switch; 240VAC, Single-Phase, 70 A, 10kAIC; rated for up to 12KVA; Wallmount; includes UPS Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker,interlock plate, lockable front panel, UL981, Black. 22"W x 24"H x 9"D; 55 lbs. | Call for Price
| 90885-C241310ECA125A12513MB | Three-Breaker Maintenance Bypass Switch; 240VAC, Single-Phase, 125 A, 10kAIC; rated for up to 20KVA; Wallmount; includes UPS Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel, UL981, Black. 22"W x 24"H x 9"D; 55 lbs. | Call for Price
| 90885-C241310ECA150A15013MB | Three-Breaker Maintenance Bypass Switch; 240VAC, Single-Phase, 150 A, 10kAIC; rated for up to 25KVA; Wallmount; includes UPS Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel, UL981, Black. 22"W x 24"H x 9"D; 55 lbs. | Call for Price
M90S Output Cords
Part Number | Model | Description | List Price
| XPC-ZLC20-620R | Optional 12" output cord, Locking C20 to 6-20 receptacle for use with M90S; 3 lbs. | 79
| XPC-ZLC20-L620R | Optional 12" output cord, Locking C20 to L6-20 receptacle for use with M90S; 3 lbs. | 79
| XPC-ZLC20-L630R | Optional 12" output cord, Locking C20 to L6-30 receptacle for use with M90S; L6-30R protected by 20A breaker; 3 lbs. | 79
| XPC-C20-L615R | Optional 12" output cord, C20 to L6-15 receptacle for use with M90S; 3 lbs. | 45
Connectivity Options
Part Number | Model | Description | List Price
90000698 | SNMP-M90S | Internal SNMP/WEB Card for use with M90S Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Packaging = 7.25"W x 6.0"D x 2.5"H, 1.0 lbs | 339
90000398 | SNMP-EMD | Environmental Monitoring Sensor to monitor room temperature and humidity - used with SNMP-M90S SNMP/WEB Card. Packaging = 7.25"W x 6.0"D x 2.5"H, 1.0 lbs | 180
90000267 | MODBUS-IN | MODBUS CARD for use with theM90S Series UPS; packaging = 7.25" x 6.0" x 2.5", 1.0 lbs | 319
90000265 | RELAY-MINI | Dry Contact RELAY CARD with DB9 & terminal block adapter; packaging = 7.25" x 6.0" x 2.5", 1.0 lbs | 120
Warranty and Service Options
Part Number | Model | Description | List Price
90001282 | 9SUS8051 | M90S 5x8 Startup and 1 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 3900
90001283 | 9SUS8052 | M90S 5x8 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 4500
90001284 | 9USUS8053 | M90S 5x8 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5100
90001285 | 9SU724051 | M90S 7x24 Startup and 1 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5070
90001286 | 9SU724052 | M90S 7x24 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5850
90001287 | 9SU724053 | M90S 7x24 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioningof UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 6630
90001288 | 9PM58 | M90S Preventative Maintenance Service, 5x8. For Zone 1 (within 100 miles of XPC Service Center). | 3500
90001289 | 9PM724 | M90S Preventative Maintenance Service, 7x24. For Zone 1 (within 100 miles of XPC Service Center). | 4550
90000538 | SVCADD | Service adder for locations further than 100 miles. | 1050

## M90S-12S Modular Single Phase
|  | Return to Index | 2024-08-01
M90S-12S Series Modular Double Conversion Split-Phase
M90S Series Ala Carte Solutions
Part Number | Model | Description | List Price
90001272 | M90S-ENC12 | XPC M90S 12-slot enclosure; Up to 48kVA/48kW; On Line - Tower configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" color touch screen, Casters, Integral Front Access Three-Breaker Maintenance Bypass switch, Floor mount bracket; Communications Module; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus) Communication Software and Cable; UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Power Modules and Battery Modules purchased separately; Dims: 23.6"W X 36"D x 79.1"H. Weight: 480 lbs. | 28400
90000693 | M90S-PWM6 | 6KVA/6KW Power Module for XPC M90S UPS; On Line- 120/208V In-120/208V Out or 120/240V In - 120/240V Out; LCD Screen, Dims: 16.3"W X 24"D x 5.2"H (3U). Weight: 38 lbs. | 4190
90001262 | M90S-BMXRV2 | Battery Module for XPC M90S UPS; Contains two battery sleeves, each containing (8) 12V 580W batteries; battery breaker; 16.3"W X 24"D x 5.2"H. Weight: 107 lbs. Note: Minimum of one battery module required for each power module used for capacity. | 2095
90000716 | M90-BC | M90S-12S Matching External Modular Battery Cabinet. Holds up to (32) x M90-BCBAT Battery Modules; 2 Year Warranty, Dims 23.6"W x 43.3"D x 79.1"H, Weight 416 lbs. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M90S-12S | 12200
90000764 | M90-BCBAT | Battery Module for M90-BC External Battery Cabinet. Contains (5) CSB HR1290 Batteries each, 4 battery modules required per string, must be purchased in multiplies of 4, (xx) battery modules will provide ___ minutes runtime @ ___kW load, Dims: 7.3"W x 38.5"D x 3.2"H, Weight 85 lbs. | 1025
90000678 | M90S12S-SEIS | Seismic Hold Down Achorage for M90S-ENC12 enclosure. Includes calculations with State of California Engineer Stamp. | 1900
90001213 | M90-CBL | Cable kit for connecting M90-BC battery cabinet to M90S-12S UPS. Includes 8’ cables and lugs. Pricing for longer length cables is available upon request. | 1050
M90S 12-Slot 18KVA Bundled Solutions
Part Number | Model | Description | List Price
Bundle | M90S-12S18K0 | XPC M90S UPS bundle; 18KVA/18KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (3) Power Modules; setup for external batteries; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure and Power Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 594 lbs. External batteries ordered seperately. | 40970
Bundle | M90S-12S18K3 | XPC M90S UPS bundle; 18KVA/18KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (3) Power Modules; (3) Battery Modules providing 9 minutes runtime @ 18KVA/18KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 915 lbs. | 47255
Bundle | M90S-12S18K4 | XPC M90S UPS bundle; 18KVA/18KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (3) Power Modules; (4) Battery Modules providing 14 minutes runtime @ 18KVA/18KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1022 lbs. | 49350
Bundle | M90S-12S18K5 | XPC M90S UPS bundle; 18KVA/18KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (3) Power Modules; (5) Battery Modules providing 18 minutes runtime @ 18KVA/18KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1129 lbs. | 51445
Bundle | M90S-12S18K6 | XPC M90S UPS bundle; 18KVA/18KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (3) Power Modules; (6) Battery Modules providing 23 minutes runtime @ 18KVA/18KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1236 lbs. | 53540
Bundle | M90S-12S18K7 | XPC M90S UPS bundle; 18KVA/18KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (3) Power Modules; (7) Battery Modules providing 27 minutes runtime @ 18KVA/18KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1343 lbs. | 55635
Bundle | M90S-12S18K8 | XPC M90S UPS bundle; 18KVA/18KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (3) Power Modules; (8) Battery Modules providing 32 minutes runtime @ 18KVA/18KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1450 lbs. | 57730
Bundle | M90S-12S18K9 | XPC M90S UPS bundle; 18KVA/18KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (3) Power Modules; (9) Battery Modules providing 37 minutes runtime @ 18KVA/18KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1557 lbs. | 59825
M90S 12-Slot 24KVA Bundled Solutions
Part Number | Model | Description | List Price
Bundle | M90S-12S24K0 | XPC M90S UPS bundle; 24KVA/24KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (4) Power Modules; setup for external batteries; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure and Power Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 632 lbs. External batteries ordered seperately. | 45160
Bundle | M90S-12S24K3 | XPC M90S UPS bundle; 24KVA/24KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (4) Power Modules; (3) Battery Modules providing 6 minutes runtime @ 24KVA/24KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 953 lbs. | 51445
Bundle | M90S-12S24K4 | XPC M90S UPS bundle; 24KVA/24KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (4) Power Modules; (4) Battery Modules providing 9 minutes runtime @ 24KVA/24KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1060 lbs. | 53540
Bundle | M90S-12S24K5 | XPC M90S UPS bundle; 24KVA/24KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (4) Power Modules; (5) Battery Modules providing 13 minutes runtime @ 24KVA/24KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1167 lbs. | 55635
Bundle | M90S-12S24K6 | XPC M90S UPS bundle; 24KVA/24KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (4) Power Modules; (6) Battery Modules providing 16 minutes runtime @ 24KVA/24KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1274 lbs. | 57730
Bundle | M90S-12S24K7 | XPC M90S UPS bundle; 24KVA/24KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (4) Power Modules; (7) Battery Modules providing 19 minutes runtime @ 24KVA/24KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1381 lbs. | 59825
Bundle | M90S-12S24K8 | XPC M90S UPS bundle; 24KVA/24KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (4) Power Modules; (8) Battery Modules providing 23 minutes runtime @ 24KVA/24KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1488 lbs. | 61920
M90S 12-Slot 30KVA Bundled Solutions
Part Number | Model | Description | List Price
Bundle | M90S-12S30K0 | XPC M90S UPS bundle; 30KVA/30KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (5) Power Modules; setup for external batteries; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure and Power Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 670 lbs. External batteries ordered seperately. | 49350
Bundle | M90S-12S30K4 | XPC M90S UPS bundle; 30KVA/30KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (5) Power Modules; (4) Battery Modules providing 7 minutes runtime @ 30KVA/30KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 991 lbs. | 57730
Bundle | M90S-12S30K5 | XPC M90S UPS bundle; 30KVA/30KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (5) Power Modules; (5) Battery Modules providing 9 minutes runtime @ 30KVA/30KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1098 lbs. | 59825
Bundle | M90S-12S30K6 | XPC M90S UPS bundle; 30KVA/30KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (5) Power Modules; (6) Battery Modules providing 12 minutes runtime @ 30KVA/30KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1205 lbs. | 61920
Bundle | M90S-12S30K7 | XPC M90S UPS bundle; 30KVA/30KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (5) Power Modules; (7) Battery Modules providing 15 minutes runtime @ 30KVA/30KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1312 lbs. | 64015
M90S 12-Slot 36KVA Bundled Solutions
Part Number | Model | Description | List Price
Bundle | M90S-12S36K0 | XPC M90S UPS bundle; 36KVA/36KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (6) Power Modules; setup for external batteries; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure and Power Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 708 lbs. External batteries ordered seperately. | 53540
Bundle | M90S-12S36K5 | XPC M90S UPS bundle; 36KVA/36KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (6) Power Modules; (5) Battery Modules providing 7 minutes runtime @ 36KVA/36KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1243 lbs. | 64015
Bundle | M90S-12S36K6 | XPC M90S UPS bundle; 36KVA/36KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (6) Power Modules; (6) Battery Modules providing 9 minutes runtime @ 36KVA/36KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1350 lbs. | 66110
M90S 12-Slot 42KVA Bundled Solutions
Part Number | Model | Description | List Price
Bundle | M90S-12S42K0 | XPC M90S UPS bundle; 42KVA/42KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (7) Power Modules; setup for external batteries; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure and Power Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 746 lbs. External batteries ordered seperately. | 57730
Bundle | M90S-12S42K5 | XPC M90S UPS bundle; 42KVA/42KW; On Line-Tower Configuration, 120/208V In/Out or 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (7) Power Modules; (5) Battery Modules providing 6 minutes runtime @ 42KVA/42KW load; ; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure, Power Modules, and Battery Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 1281 lbs. | 68205
M90S 12-Slot 48KVA Bundled Solutions
Part Number | Model | Description | List Price
Bundle | M90S-12S48K0 | XPC M90S UPS bundle; 48KVA/48KW; On Line-Tower Configuration, 120/240V In/Out, Hardwired in/out, 10" Color Touchscreen, Casters, Floor mount bracket; Communications Module; Bundle includes M90S-ENC12 12-Slot Enclosure with Integral Front Access Maintenance Bypass, (8) Power Modules; setup for external batteries; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC A, RoHS; Start-up (5x8), 3 year parts and 2-year on-site labor warranty are included (USA and Canada). Enclosure and Power Modules shipped seperately. Dims: 23.6"W X 36"D x 79.1"H. Weight: 746 lbs. External batteries ordered seperately. | 61920
M90-BC Modular Battery Cabinet Bundles
Part Number | Model | Description | List Price
Bundle | M90-BC-04B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (4) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 756 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M90S-12S Cable Available. | 16300
Bundle | M90-BC-08B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (8) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 1096 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M90S-12S Cable Available. | 20400
Bundle | M90-BC-12B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (12) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 1436 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M90S-12S Cable Available. | 24500
Bundle | M90-BC-16B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (16) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 1776 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M90S-12S Cable Available. | 28600
Bundle | M90-BC-20B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (20) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 2116 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M90S-12S Cable Available. | 32700
Bundle | M90-BC-24B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (24) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 2456 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M90S-12S Cable Available. | 36800
Bundle | M90-BC-28B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (28) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 2796 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M90S-12S Cable Available. | 40900
Bundle | M90-BC-32B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (32) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Each battery string (4 modules) protected by a 100A breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 3136 lbs. Battery modules shipped on separate pallet. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M90S-12S Cable Available. | 45000
Connectivity Options
Part Number | Model | Description | List Price
90000698 | SNMP-M90S | Internal SNMP/WEB Card for use with M90S Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Packaging = 7.25"W x 6.0"D x 2.5"H, 1.0 lbs | 339
90000398 | SNMP-EMD | Environmental Monitoring Sensor to monitor room temperature and humidity - used with SNMP-M90S SNMP/WEB Card. Packaging = 7.25"W x 6.0"D x 2.5"H, 1.0 lbs | 180
90000267 | MODBUS-IN | MODBUS CARD for use with the P90L Series UPS; packaging = 7.25" x 6.0" x 2.5", 1.0 lbs | 319
Warranty and Service Options
Part Number | Model | Description | List Price
90001282 | M90S12SSU583 | Upgrade standard warranty to 5x8 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance and (1) PM (5X8) to be perfromed at beginning of year three. | 6500
90001249 | M90S12SSU72 | Upgrade Standard 5x8 Warranty to 7x24 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 2800
90001284 | M90S12SSU73 | Upgrade Standard Warranty to 7x24 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioningof UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance and (1) PM (7x24) to be perfromed at beginning of year three. | 9300
90001285 | M90S12S1YREE | M90S-12S One Year extension of factory on-site warranty, electronics only. Covers parts and labor, extending the standard warranty by 1 year. Includes (1) PM (7x24) to be perfromed at beginning of the extension year. For Zone 1 (within 100 miles of XPC Service Center). | 8800
90001286 | M90S12SSPM7 | M90S-12S Preventative Maintenance Service, 7x24. For Zone 1 (within 100 miles of XPC Service Center). | 5850
90000538 | SVCADD | Service adder for locations further than 100 miles. | 1200

## Li90
|  | Return to Index | 2025-09-15
Li90 Series Double Conversion 3-Phase (with Lithium Batteries)
Part Number | Model | Description | List Price
Bundle | Li90-10k1 | Xtreme Power Li90 Series online 10KVA/10KW, 208/120 VAC three-phase UPS with one internal lithium battery module for 15 minutes full load runtime. Includes color touch screen display, static switch, and maintenance bypass switch ; up to 40A charge current, 94.5% efficiency in online mode or 99% efficiency in ECO mode; standard local EPO, RS485 ports; (5) output dry contacts; (2) input dry contacts; (1) card slot for Web/SNMP; UL-1778 (TUV), UL 38.3, UL1973 ; 2 Year On-site UPS Warranty (USA and Canada); 5 Year Battery Warranty; 5x8 Start-up included. Can accommodate up to three battery modules for extended runtimes; 12.6" W x 35.2" D x 49.2" H. 287 lbs. | 29500
Bundle | Li90-10k2 | Xtreme Power Li90 Series online 10KVA/10KW, 208/120 VAC three-phase UPS with two internal lithium battery modules for 30 minutes full load runtime. Includes color touch screen display, static switch, and maintenance bypass switch ; up to 40A charge current, 94.5% efficiency in online mode or 99% efficiency in ECO mode; standard local EPO, RS485 ports; (5) output dry contacts; (2) input dry contacts; (1) card slot for Web/SNMP; UL-1778 (TUV), UL 38.3, UL1973 ; 2 Year On-site UPS Warranty (USA and Canada); 5 Year Battery Warranty; 5x8 Start-up included. Can accommodate up to three battery modules for extended runtimes; 12.6" W x 35.2" D x 49.2" H. 367 lbs. | 38000
Bundle | Li90-10k3 | Xtreme Power Li90 Series online 10KVA/10KW, 208/120 VAC three-phase UPS with three internal lithium battery modules for 45 minutes full load runtime. Includes color touch screen display, static switch, and maintenance bypass switch ; up to 40A charge current, 94.5% efficiency in online mode or 99% efficiency in ECO mode; standard local EPO, RS485 ports; (5) output dry contacts; (2) input dry contacts; (1) card slot for Web/SNMP; UL-1778 (TUV), UL 38.3, UL1973 ; 2 Year On-site UPS Warranty (USA and Canada); 5 Year Battery Warranty; 5x8 Start-up included. 12.6" W x 35.2" D x 49.2" H. 447 lbs. | 46500
Bundle | Li90-20k2 | Xtreme Power Li90 Series online 20KVA/20KW, 208/120 VAC three-phase UPS with two internal lithium battery modules for 15 minutes full load runtime. Includes color touch screen display, static switch, and maintenance bypass switch ; up to 40A charge current, 94.5% efficiency in online mode or 99% efficiency in ECO mode; standard local EPO, RS485 ports; (5) output dry contacts; (2) input dry contacts; (1) card slot for Web/SNMP; UL-1778 (TUV), UL 38.3, UL1973 ; 2 Year On-site UPS Warranty (USA and Canada); 5 Year Battery Warranty; 5x8 Start-up included. Can accommodate up to three battery modules for extended runtimes; 12.6" W x 35.2" D x 49.2" H. 387 lbs. | 45000
Bundle | Li90-20k3 | Xtreme Power Li90 Series online 20KVA/20KW, 208/120 VAC three-phase UPS with three internal lithium battery module for 22 minutes full load runtime. Includes color touch screen display, static switch, and maintenance bypass switch ; up to 40A charge current, 94.5% efficiency in online mode or 99% efficiency in ECO mode; standard local EPO, RS485 ports; (5) output dry contacts; (2) input dry contacts; (1) card slot for Web/SNMP; UL-1778 (TUV), UL 38.3, UL1973 ; 2 Year On-site UPS Warranty (USA and Canada); 5 Year Battery Warranty; 5x8 Start-up included. 12.6" W x 35.2" D x 49.2" H. 467 lbs. | 53500
Bundle | Li90-30k3 | Xtreme Power Li90 Series online 30KVA/30KW, 208/120 VAC three-phase UPS with three internal lithium battery module for 15 minutes full load runtime. Includes color touch screen display, static switch, and maintenance bypass switch ; up to 40A charge current, 94.5% efficiency in online mode or 99% efficiency in ECO mode; standard local EPO, RS485 ports; (5) output dry contacts; (2) input dry contacts; (1) card slot for Web/SNMP; UL-1778 (TUV), UL 38.3, UL1973 ; 2 Year On-site UPS Warranty (USA and Canada); 5 Year Battery Warranty; 5x8 Start-up included. 12.6" W x 35.2" D x 49.2" H. 483 lbs. | 59000
Connectivity Options
Part Number | Model | Description | List Price
90001245 | SNMP-2PG1 | Internal two port SNMP/WEB Card for use with X90, M90C, M90, M90L E91, and M90S Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-TMPH temperature and humidity probe; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 715
90000398 | SNMP-TMPH | Temperature and humidity Probe - used with SNMP-2PG1 SNMP/WEB Card. Packaging = 7.25"W x 6.0"D x 2.5"H, 1.0 lbs | 329
Service Options
Part Number | Model | Description | List Price
90001348 | Li901U58 | Li90 UPS Warranty Upgrade from 2-Year 5x8 On-Site to 3-Year 5x8 On-Site. Includes (1) 5x8 PM to be beformed at the beginning of year three. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5500
90001349 | Li902U58 | Li90 UPS Warranty Upgrade from 2-Year 5x8 On-Site to 5-Year 5x8 On-Site. Includes (2) 5x8 PMs to be beformed at the beginning of year three and beginning of year 5. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 13500
90001350 | Li90724 | Li90 UPS Warranty Upgrade from 2-Year 5x8 On-Site to 2-Year 7x24 On-Site. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 2800
90001351 | li901U724 | Li90 UPS Warranty Upgrade from 2-Year 5x8 On-Site to 3-Year 7x24 On-Site. Includes (1) 7x24 PM to be beformed at the beginning of year three. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 8000
90001352 | Li90PM24 | Li90 Preventative Maintenance Service, 7x24. For Zone 1 (within 100 miles of XPC Service Center). | 5800
90000538 | SVCADD | Service adder for locations further than 100 miles. | 1050

## E91
|  | Return to Index | 2025-09-15
E91 Series Double Conversion 3-Phase (with Internal Batteries)
Part Number | Model | Description | List Price
90000975 | E91-10K | Xtreme Power E91 Series online 10KVA/10KW, 208/120 VAC three-phase UPS with 2 strings of internal batteries for 11 minutes full load runtime. Includes color touch screen display, static switch, and maintenance bypass switch ; up to 12A charge current, 94% efficiency in online mode or 98% efficiency in ECO mode; standard RS232, EPO, RS485, and USB communication ports; (1) card slot for Web/SNMP or Relay cards; UL-1778 (TUV), cUL, FCCA, Energy Star 2.0 ; 2 Year Standard Warranty (USA and Canada); Start-up and onsite labor is not included; Can accommodate external battery packs for extended runtimes; 9.9" W x 26.3" D x 32.3" H. 273 lbs. | 10800
90000976 | E91-15K | Xtreme Power E91 Series online 15KVA/15KW, 208/120 VAC three-phase UPS with 3 strings of internal batteries for 11 minutes full load runtime. Includes color touch screen display, static switch, and maintenance bypass switch ; up to 12A charge current, 94% efficiency in online mode or 98% efficiency in ECO mode; standard RS232, EPO, RS485, and USB communication ports; (1) card slot for Web/SNMP or Relay cards; UL-1778 (TUV), cUL, FCCA, Energy Star 2.0 ; 2 Year Standard Warranty (Usa and Canada); Start-up and onsite labor is not included; Can accommodate external battery packs for extended runtimes; 11.9" W x 34" D x 40.2" H. 306 lbs. | 12700
90000977 | E91-20K | Xtreme Power E91 Series online 20KVA/20KW, 208/120 VAC three-phase UPS with 3 strings of internal batteries for 7 minutes full load runtime. Includes color touch screen display, static switch, and maintenance bypass switch ; up to 12A charge current, 94% efficiency in online mode or 98% efficiency in ECO mode; standard RS232, EPO, RS485, and USB communication ports; (1) card slot for Web/SNMP or Relay cards; UL-1778 (TUV), cUL, FCCA, Energy Star 2.0 ; 2 Year Standard Warranty (USA and Canada); Start-up and onsite labor is not included; Can accommodate external battery packs for extended runtimes; 11.9" W x 34" D x 40.2" H. 306 lbs. | 13600
90000980 | E91-20KL | Xtreme Power E91 Series online 20KVA/20KW, 208/120 VAC three-phase UPS with no internal batteries. Includes color touch screen display, static switch, and maintenance bypass switch ; up to 12A charge current, 94% efficiency in online mode or 98% efficiency in ECO mode; standard RS232, EPO, RS485, and USB communication ports; (1) card slot for Web/SNMP or Relay cards; UL-1778 (TUV), cUL, FCCA, Energy Star 2.0 ; 2 Year Standard Warranty (USA and Canada); Start-up and onsite labor is not included; 11.9" W x 34" D x 40.2" H. 296 lbs. External battery packs must be ordered seperately. | 11800
90000979 | E91-30K | Xtreme Power E91 Series online 30KVA/30KW, 208/120 VAC three-phase UPS with 3 strings of internal batteries for 6 minutes full load runtime. Includes color touch screen display, static switch, and maintenance bypass switch; Front access only design; up to 16A charge current, 94% efficiency in online mode or 98% efficiency in ECO mode; standard RS232, EPO, RS485, and USB communication ports; (1) card slot for Web/SNMP or Relay cards; UL-1778 (TUV), cUL, FCC; 2 Year Standard Warranty (USA and Canada); Start-up and onsite labor is not included; Can accommodate external battery packs for extended runtimes; 23.6" W x 36.3" D x 65.6" H. 496 lbs. | 21800
90001234 | E91-30K4 | Xtreme Power E91 Series online 30KVA/30KW, 208/120 VAC three-phase UPS with 4 strings of internal batteries for 9 minutes full load runtime. Includes color touch screen display, static switch, and maintenance bypass switch; Front access only design; up to 16A charge current, 94% efficiency in online mode or 98% efficiency in ECO mode; standard RS232, EPO, RS485, and USB communication ports; (1) card slot for Web/SNMP or Relay cards; UL-1778 (TUV), cUL, FCC; 2 Year Standard Warranty (USA and Canada); Start-up and onsite labor is not included; Can accommodate external battery packs for extended runtimes; 23.6" W x 36.3" D x 65.6" H. 549 lbs. | 23700
90000981 | E91-30KL | Xtreme Power E91 Series online 30KVA/30KW, 208/120 VAC three-phase UPS no internal batteries. Includes color touch screen display, static switch, and maintenance bypass switch; Front access only design; up to 16A charge current, 94% efficiency in online mode or 98% efficiency in ECO mode; standard RS232, EPO, RS485, and USB communication ports; (1) card slot for Web/SNMP or Relay cards; UL-1778 (TUV), cUL, FCC; 2 Year Standard Warranty (USA and Canada); Start-up and onsite labor is not included; 23.6" W x 36.3" D x 65.6" H. 419 lbs. External battery packs must be ordered seperately. | 17000
90000980 | E91-40K | Xtreme Power E91 Series online 40KVA/40KW, 208/120 VAC three-phase UPS with 4 strings of internal batteries for 6 minutes full load runtime. Includes color touch screen display, static switch, and maintenance bypass switch; Front access only design; up to 16A charge current, 94% efficiency in online mode or 98% efficiency in ECO mode; standard RS232, EPO, RS485, and USB communication ports; (1) card slot for Web/SNMP or Relay cards; UL-1778 (TUV), cUL, FCC; 2 Year Standard Warranty (USA and Canada); Start-up and onsite labor is not included; Can accommodate external battery packs for extended runtimes; 23.6" W x 36.3" D x 65.6" H. 551 lbs. | 25300
90000982 | E91-40KL | Xtreme Power E91 Series online 40KVA/40KW, 208/120 VAC three-phase UPS with no internal batteries. Includes color touch screen display, static switch, and maintenance bypass switch; Front access only design; up to 16A charge current, 94% efficiency in online mode or 98% efficiency in ECO mode; standard RS232, EPO, RS485, and USB communication ports; (1) card slot for Web/SNMP or Relay cards; UL-1778 (TUV), cUL, FCC; 2 Year Standard Warranty (USA and Canada); Start-up and onsite labor is not included; 23.6" W x 36.3" D x 65.6" H. 539 lbs. External battery packs must be ordered seperately. | 18500
External Battery for use with E91 UPS (With Batteries)
Part Number | Model | Description | List Price
90000984 | EBP09-2 | Line and Match External Battery Pack for E91 10KVA, 15kVA, and 20kVA UPS. Includes (40) 12V 9AH batteries; Up to four battery packs per UPS can be used for extended runtime applications; (_) battery packs provides (__) minutes of runtime @ __KW load. 11.9"W x 34"D x 40.2"H. 310 lbs. | 6100
90000985 | EBP09-5 | Line and Match External Battery Pack for E91 10KVA, 15kVA, and 20kVA UPS. Includes (100) 12V 9AH batteries; Up to four battery packs per UPS can be used for extended runtime applications; (_) battery packs provides (__) minutes of runtime @ __KW load. 11.9"W x 34"D x 40.2"H. 670 lbs. | 9950
90000986 | EBP10-5 | Line and Match External Battery Pack for E91 30KVA/30KW or 40KVA/40KW UPS. Includes (100) 12V 580W batteries; Up to four battery packs per UPS can be used for extended runtime applications; (_) battery packs provides (__) minutes of runtime @ __KW load. 11.9"W x 34"D x 40.2"H. 770 lbs. | 11700
PDU Options (Rear mounted)
Part Number | Model | Description | List Price
90001023 | E91-PDU1 | E91 rear mounted PDU. Configured with (4) L21-20R outlets each protected by a 20A breaker. 9.5"W x 4.3"D x 11.6"H; 15 lbs *Optional Power Distributions Units may not be used with external maintenance bypass. | 1350
90001024 | E91-PDU2 | E91 rear mounted PDU. Configured with (4) L21-30R outlets each protected by a 30A breaker. 9.5"W x 4.3"D x 11.6"H; 15 lbs *Optional Power Distributions Units may not be used with external maintenance bypass. | 1500
External Maintenance Bypass Options (wallmount)
Part Number | Model | Description | List Price
| 90885-C208310ECA040A04013MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 40 A, 10kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 22"W x 24"H x 9"D; 55 lbs. For use with E91 10kVA UPS | Call For Price
| 90885-C208310ECA060A06013MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 60 A, 10kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 22"W x 24"H x 9"D; 55 lbs. For Use with E91 and all M90 Family 15kVA UPS | Call For Price
| 90885-C208310ECA080A08013MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 80 A, 10kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 22"W x 24"H x 9"D; 55 lbs. For Use with E91 and all M90 Family 20kVA UPS | Call For Price
| 90880-C208322ECA125A12502MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 125 A, 22kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 30"W x 36"H x 10"D; 110 lbs. For Use with E91 and all M90 Family 30kVA UPS | Call For Price
| 90880-C208322ECA150A15002MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 150 A, 22kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 30"W x 36"H x 10"D; 110 lbs. For Use with E91 40kVA UPS | Call For Price
Note: | E91 does not have Contacts to support SKRU.
Connectivity Options
Part Number | Model | Description | List Price
90001245 | SNMP-2PG1 | Internal two port SNMP/WEB Card for use with X90, M90C, M90, M90L E91, and M90S Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-TMPH temperature and humidity probe; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 715
90000267 | MODBUS-IN | MODBUS CARD for use with the E91, M90(U) and X90 Series UPS; packaging = 7.25" x 6" x 2.5", 1 lbs | 319
90000398 | SNMP-TMPH | Temperature and humidity Probe - used with SNMP-2PG1 SNMP/WEB Card. Packaging = 7.25"W x 6.0"D x 2.5"H, 1.0 lbs | 329
90000265 | RELAY-MINI | Dry Contact RELAY CARD with DB9 & terminal block adapter; packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 120
Service Options
Part Number | Model | Description | List Price
90001011 | E91SUS81 | E91 5x8 Startup and 1 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 3900
90001005 | E91SUS82 | E91 5x8 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 4500
90001006 | E91SUS83 | E91 5x8 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 7400
90001012 | E91SU7241 | E91 7x24 Startup and 1 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5070
90001007 | E91SU7242 | E91 7x24 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5850
90001235 | E91SU7243 | E91 7x24 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioningof UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 9620
90001236 | E91PM58 | E91 Preventative Maintenance Service, 5x8. For Zone 1 (within 100 miles of XPC Service Center). | 3500
90001010 | E91PM724 | E91 Preventative Maintenance Service, 7x24. For Zone 1 (within 100 miles of XPC Service Center). | 4550
90000538 | SVCADD | Service adder for locations further than 100 miles. | 1050

## M90C
|  | Return to Index | 2025-09-15
M90C Series Modular Double Conversion Three-Phase
M90C Series Ala Carte Solutions
Part Number | Model | Description | List Price
90001032 | M90C-ENC2 | XPC M90C 2-slot enclosure; 5kVA/5kW or 8kVA/8kW; On Line - Rack Mount or tower configuration, 120/208V Three-Phase In/Out , Hardwired in/out, Integral Rear Mounted Maintenance Bypass switch, RS-232, USB, EPO, intelligent slot for optional card (Web/SNMP, Relay, Modbus); Communication Software and Cable; UL-1778 (TUV), cUL, FCC, RoHS, TAA Compliant; 2 year UPS and battery warranty (USA and Canada). Power Module and Battery Module purchased separately; Unit Dims: 17.3"W X 31.5"D x 10.5"H. Weight: 38 lbs. | 2300
90001218 | M90C-ENC6 | XPC M90C 6-slot enclosure; Up to 24kVA/24kW; On Line - Tower configuration, 120/208V Three-Phase In/Out , Hardwired in/out, Large LCD Screen, Casters, Integral Front Access Maintenance Bypass switch, Floor mount bracket; Communications Module; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus) Communication Software and Cable; UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Power Modules, Battery Modules, and Blank Panels purchased separately; Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 169 lbs. | 8000
90001211 | M90C-PWM5 | 5KVA/5KW Power Module for XPC M90C UPS; On Line- 120/208V Three-Phase In- Out; LCD Screen, Dims: 16.3"W X 24"D x 5.2"H (3U). Weight: 38 lbs. | 4900
90001029 | M90C-PWM8 | 8KVA/8KW Power Module for XPC M90C UPS; On Line- 120/208V Three-Phase In- Out; LCD Screen, Dims: 16.3"W X 24"D x 5.2"H (3U). Weight: 38 lbs. | 5700
90001262 | M90S-BMXRV2 | Battery Module for XPC M90S UPS; Contains two battery sleeves, each containing (8) 12V 580W batteries; battery breaker; 16.3"W X 24"D x 5.2"H. Weight: 107 lbs. Note: Minimum of one battery module required for each power module used for capacity. | 2095
90000696 | M90S-BC7 | XPC M90S External Battery Enclosure; 7-slot enclosure holds up to (7) M90S-BMXR battery modules; Includes Casters. Battery Modules and Blank Panels purchased separately; Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 162 lbs. | 4935
90000719 | M90S-CB | Caster Base for M90C-ENC2 or M90S-ENC2. Locking casters. Dims: 17"W X 24"D x 4.0"H. Weight: 15 lbs. | 610
90000703 | M90S-BP | M90C or M90S Matching Blank Panel covers front of unused slots. Dims: 16.5"W X 2"D x 5.2"H. Weight: 5 lbs. | 63
90000695 | M90S-RAIL2S | M90S Rail Kit for M90C-ENC2 or M90S-ENC2 2-slot enclosure. Dims: 20"W X 4"D x 2.5"H. Weight: 5 lbs. | 155
90001219 | XPC-L21-20P | Optional 8' Input cord, Terminal to L21-20P for use with M90C-5kW; 10 lbs. | 420
90001220 | XPC-L21-30P | Optional 8' Input cord, Terminal to L21-30P for use with M90C-8kW; 10 lbs. | 420
| M90C6S-SEIS | Seismic Hold Down Achorage for M90C-ENC6 enclosure. Includes calculations with State of California Engineer Stamp. | 1900
M90C Series Optional Receptacle Panels (6S = up to 4 RP), (2S = up to 1 RP)
Part Number | Model | Description | List Price
90000699 | M90S-RPA | XPC M90C Optional Receptacle Panel for M90C-6S. Contains (8) 5-20R receptacles. Mounts to rear of UPS Chassis. Weight: 5 lbs. | 295
90000700 | M90S-RPB | XPC M90C Optional Receptacle Panel for M90C-6S. Contains (2) C19 and (4) 5-20R receptacles. Mounts to rear of UPS Chassis. Weight: 5 lbs. | 295
90000701 | M90S-RPC | XPC M90C Optional Receptacle Panel for M90C-6S. Contains (1) L6-30R and (2) C19 receptacles. Mounts to rear of UPS Chassis. Weight: 5 lbs. | 295
90000703 | M90S-RPD | XPC M90C Optional Receptacle Panel for M90C-6S. Contains (1) L14-30R and (2) C19 receptacles. Mounts to rear of UPS Chassis. Weight: 5 lbs. | 295
Bundle | M90S-RPE | XPC M90C Optional Receptacle Panel for M90C-6S. Contains (2) L6-20R and (4) 5-20R receptacles. Mounts to rear of UPS Chassis. Weight: 5 lbs. | 453
Bundle | M90S-RPF | XPC M90C Optional Receptacle Panel for M90C-6S. Contains (1) L6-30R, (1) L6-20R and (4) 5-20R receptacles. Mounts to rear of UPS Chassis. L6-30R protected by 20A breaker; Weight: 5 lbs. | 453
Bundle | M90S-RPG | XPC M90C Optional Receptacle Panel for M90C-6S. Contains (1) L6-30R and (2) L6-20R receptacles. Mounts to rear of UPS Chassis. Weight: 5 lbs. | 453
Bundle | M90S-RPH | XPC M90C Optional Receptacle Panel for M90C-6S. Contains (3) L6-30R receptacles. Mounts to rear of UPS Chassis. (2) L6-30R protected by 20A breakers; Weight: 5 lbs. | 453
90001058 | M90C-RPI | XPC M90C Optional Receptacle Panel for M90C-2S or M90C-6S. Contains (1) L21-20R receptacle protected by a 20A breaker. Mounts to rear of UPS Chassis. Weight: 6 lbs. | 395
90001059 | M90C-RPJ | XPC M90C Optional Receptacle Panel for M90C-2S or M90C-6S. Contains (1) L21-30R receptacle protected by a 30A breaker. Mounts to rear of UPS Chassis. Weight: 6 lbs. | 395
90001060 | M90C-RPK | XPC M90C Optional Receptacle Panel for M90C-2S or M90C-6S. Contains (2) L21-20R receptacles. Mounts to rear of UPS Chassis. Weight: 6 lbs. | 395
90001061 | M90C-RPL | XPC M90C Optional Receptacle Panel for M90C-2S or M90C-6S. Contains (2) L21-30R receptacles. Mounts to rear of UPS Chassis. Weight: 6 lbs. | 395
M90C-2S Series Hardwired Bundled Solutions
Part Number | Model | Description | List Price
Bundle | M90C-2S5K | XPC M90C UPS bundle; 5kVA/5kW; On Line-Rackmount Configuration, 120/208V Three-Phase In/Out, Hardwired in/out. Bundle includes M90C-ENC2 2-Slot Enclosure with Integral Maintenance Bypass, Rackmount rails; (1) 5kVA/5kW Power Module and (1) Battery Module providing 12 minutes runtime @ 5KVA/5KW load; RS-232, USB, EPO, intelligent slot for optional card (Web/SNMP, Relay, Modbus; ) Communication Software and Cable; UL-1778 (TUV), cUL, FCC, RoHS, TAA Compliant; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 17.5"W X 33.7"D x 10.5"H. Weight: 185 lbs. | 9450
Bundle | M90C-2S5KT | XPC M90C UPS bundle; 5kVA/5kW; On-Line Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out. Bundle includes M90C-ENC2 2-Slot Enclosure with Integral Maintenance Bypass, Caster Base; (1) 5kVA/5kW Power Module and (1) Battery Module providing 12 minutes runtime @ 5KVA/5KW load; RS-232, USB, EPO, intelligent slot for optional card (Web/SNMP, Relay, Modbus; ) Communication Software and Cable; UL-1778 (TUV), cUL, FCC, RoHS, TAA Compliant; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 17.5"W X 33.7"D x 14.5"H. Weight: 198 lbs. | 9905
Bundle | M90C-2S8K | XPC M90C UPS bundle; 8kVA/8kW; On Line-Rackmount Configuration, 120/208V Three-Phase In/Out, Hardwired in/out. Bundle includes M90C-ENC2 2-Slot Enclosure with Integral Maintenance Bypass, Rackmount rails; (1) 8kVA/8kW Power Module and (1) Battery Module providing 6 minutes runtime @ 8KVA/8KW load; RS-232, USB, EPO, intelligent slot for optional card (Web/SNMP, Relay, Modbus; ) Communication Software and Cable; UL-1778 (TUV), cUL, FCC, RoHS, TAA Compliant; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 17.5"W X 33.5"D x 10.5"H. Weight: 185 lbs. | 10250
Bundle | M90C-2S8KT | XPC M90C UPS bundle; 8kVA/8kW; On-Line Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out. Bundle includes M90C-ENC2 2-Slot Enclosure with Integral Maintenance Bypass, Caster Base; (1) 8kVA/8kW Power Module and (1) Battery Module providing 12 minutes runtime @ 8KVA/8KW load; RS-232, USB, EPO, intelligent slot for optional card (Web/SNMP, Relay, Modbus; ) Communication Software and Cable; UL-1778 (TUV), cUL, FCC, RoHS, TAA Compliant; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 14.5"H. Weight: 198 lbs. | 10705
M90C 6-Slot 5KVA Hardwired Bundled Solutions
Part Number | Model | Description | List Price
| M90C-6S5K1 | XPC M90C UPS bundle; 5KVA/5KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) 5kVA Power Module, (1) Battery Module providing 12 minutes runtime @ 5KVA/5KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 314 lbs. | 15247
| M90C-6S5K2 | XPC M90C UPS bundle; 5KVA/5KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) 5K Power Module, (2) Battery Modules providing 28 minutes runtime @ 5KVA/5KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 421 lbs. | 17279
| M90C-6S5K3 | XPC M90C UPS bundle; 5KVA/5KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) 5K Power Module, (3) Battery Modules providing 46 minutes runtime @ 5KVA/5KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 528 lbs. | 19311
| M90C-6S5K4 | XPC M90C UPS bundle; 5KVA/5KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) 5K Power Module, (4) Battery Modules providing 66 minutes runtime @ 5KVA/5KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 635 lbs. | 21343
| M90C-6S5K5 | XPC M90C UPS bundle; 5KVA/5KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) 5K Power Module, (5) Battery Modules providing 86 minutes runtime @ 5KVA/5KW load; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 742 lbs. | 23375
M90C 6-Slot 8KVA Hardwired Bundled Solutions
Part Number | Model | Description | List Price
| M90C-6S8K1 | XPC M90C UPS bundle; 8KVA/8KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) 8kVA Power Module, (1) Battery Module providing 6 minutes runtime @ 8KVA/8KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 314 lbs. | 16047
| M90C-6S8K2 | XPC M90C UPS bundle; 8KVA/8KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) 8kVA Power Module, (2) Battery Module providing 16 minutes runtime @ 8KVA/8KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 421 lbs. | 18079
| M90C-6S8K3 | XPC M90C UPS bundle; 8KVA/8KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) 8kVA Power Module, (3) Battery Module providing 26 minutes runtime @ 8KVA/8KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 528 lbs. | 20111
| M90C-6S8K4 | XPC M90C UPS bundle; 8KVA/8KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) 8kVA Power Module, (4) Battery Module providing 37 minutes runtime @ 8KVA/8KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 635 lbs. | 22143
| M90C-6S8K5 | XPC M90C UPS bundle; 8KVA/8KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (1) 8kVA Power Module, (5) Battery Module providing 49 minutes runtime @ 8KVA/8KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 742 lbs. | 24175
M9C 6-Slot 10KVA Hardwired Bundled Solutions
Part Number | Model | Description | List Price
| M90C-6S10K2 | XPC M90C UPS bundle; 10KVA/10KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (2) 5kVA Power Modules, (2) Battery Module providing 12 minutes runtime @ 10KVA/10KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 459 lbs. | 22116
| M90C-6S10K3 | XPC M90C UPS bundle; 10KVA/10KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (2) 5kVA Power Modules, (3) Battery Module providing 20 minutes runtime @ 10KVA/10KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 566 lbs. | 24148
| M90C-6S10K4 | XPC M90C UPS bundle; 10KVA/10KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (2) 5kVA Power Modules, (4) Battery Module providing 28 minutes runtime @ 10KVA/10KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 673 lbs. | 26180
M90C 6-Slot 15KVA Hardwired Bundled Solutions
Part Number | Model | Description | List Price
| M90C-6S15K2 | XPC M90C UPS bundle; 15KVA/15KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (3) 5kVA Power Module, (2) Battery Module providing 7 minutes runtime @ 15KVA/15KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 604 lbs. | 26953
| M90C-6S15K3 | XPC M90C UPS bundle; 15KVA/15KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (3) 5kVA Power Module, (3) Battery Module providing 12 minutes runtime @ 15KVA/15KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 711 lbs. | 28985
M90C 6-Slot 16KVA Hardwired Bundled Solutions
Part Number | Model | Description | List Price
| M90C-6S16K2 | XPC M90C UPS bundle; 16KVA/16KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (2) 8kVA Power Module, (2) Battery Module providing 6 minutes runtime @ 16KVA/16KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 459 lbs. | 23716
| M90C-6S16K3 | XPC M90C UPS bundle; 16KVA/16KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (2) 8kVA Power Module, (3) Battery Module providing 11 minutes runtime @ 16KVA/16KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 566 lbs. | 25748
| M90C-6S16K4 | XPC M90C UPS bundle; 16KVA/16KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (2) 8kVA Power Module, (4) Battery Module providing 16 minutes runtime @ 16KVA/16KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 673 lbs. | 27780
M9C 6-Slot 24KVA Hardwired Bundled Solutions
Part Number | Model | Description | List Price
| M90C-6S24K3 | XPC M90C UPS bundle; 24KVA/24KW; On Line-Tower Configuration, 120/208V Three-Phase In/Out, Hardwired in/out, Large LCD Screen, Casters, Floor mount bracket; Communications Module; Bundle includes M90C-ENC6 6 Slot Enclosure with Integral Front Access Maintenance Bypass, (3) 8kVA Power Module, (3) Battery Module providing 6 minutes runtime @ 24KVA/24KW load, blank panels; RS-232, USB, dry contacts, EPO, (2) intelligent slots for optional cards (Web/SNMP, Relay, Modbus); Communication Software and Cable. UL-1778 (TUV), cUL, FCC, RoHS; 2 year UPS and battery warranty (USA and Canada). Enclosure, Power Module, and Battery Module shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 711 lbs. | 31385
M90C Battery Cabinet Bundles
Part Number | Model | Description | List Price
| M90S-BC7-1 | XPC M90C Battery Cabinet bundle; Includes XPC M90S-BC7 7 Slot External Battery Enclosure; (1) battery module; (6) blank panels; DC Breaker; Casters. 2 year battery warranty (USA and Canada). Increases runtime to __ minutes runtime @ __KVA/__KW load; Enclosure and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 269 lbs | 7408
| M90S-BC7-2 | XPC M90C Battery Cabinet bundle; Includes XPC M90S-BC7 7 Slot External Battery Enclosure; (2) battery module; (5) blank panels; DC Breaker; Casters. 2 year battery warranty (USA and Canada). Increases runtime to __ minutes runtime @ __KVA/__KW load; Enclosure and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 376 lbs | 9440
| M90S-BC7-3 | XPC M90C Battery Cabinet bundle; Includes XPC M90S-BC7 7 Slot External Battery Enclosure; (3) battery module; (4) blank panels; DC Breaker; Casters. 2 year battery warranty (USA and Canada). Increases runtime to __ minutes runtime @ __KVA/__KW load; Enclosure and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 483 lbs | 11472
| M90S-BC7-4 | XPC M90C Battery Cabinet bundle; Includes XPC M90S-BC7 7 Slot External Battery Enclosure; (4) battery module; (3) blank panels; DC Breaker; Casters. 2 year battery warranty (USA and Canada).. Increases runtime to __ minutes runtime @ __KVA/__KW load; Enclosure and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 590 lbs | 13504
| M90S-BC7-5 | XPC M90C Battery Cabinet bundle; Includes XPC M90S-BC7 7 Slot External Battery Enclosure; (5) battery module; (2) blank panels; DC Breaker; Casters. 2 year battery warranty (USA and Canada). Increases runtime to __ minutes runtime @ __KVA/__KW load; Enclosure and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 697 lbs | 15536
| M90S-BC7-6 | XPC M90C Battery Cabinet bundle; Includes XPC M90S-BC7 7 Slot External Battery Enclosure; (6) battery module; (1) blank panel; DC Breaker; Casters. 2 year battery warranty (USA and Canada). Increases runtime to __ minutes runtime @ __KVA/__KW load; Enclosure and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 804 lbs | 17568
| M90S-BC7-7 | XPC M90C Battery Cabinet bundle; Includes XPC M90S-BC7 7 Slot External Battery Enclosure; (7) battery modules; DC Breaker; Casters. 2 year battery warranty (USA and Canada).. Increases runtime to __ minutes runtime @ __KVA/__KW load; Enclosure and Battery Modules shipped seperately. Dims: 17.4"W X 33.7"D x 45.5"H. Weight: 911 lbs | 19600
Connectivity Options
Part Number | Model | Description | List Price
90001245 | SNMP-2PG1 | Internal two port SNMP/WEB Card for use with M90C, M90 and M90L Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-TMPH teperature and humidity probe; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 715
90000398 | SNMP-TMPH | Temperature and humidity Probe - used with SNMP-2PG1 SNMP/WEB Card. Packaging = 7.25"W x 6.0"D x 2.5"H, 1.0 lbs | 329
90000267 | MODBUS-IN | MODBUS CARD for use with the XPC UPS; packaging = 7.25" x 6.0" x 2.5", 1.0 lbs | 319
Warranty and Service Options
Part Number | Model | Description | List Price
90001290 | MCSU58OS1 | M90C 5x8 Startup and 1 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 3900
90001291 | MCSU58OS2 | M90C 5x8 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 4500
90001292 | MCSU58OS3 | M90C 5x8 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5100
90001293 | MCSU724OS1 | M90C 7x24 Startup and 1 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5070
90001294 | MCSU724OS2 | M90C 7x24 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioning of UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 5850
90001295 | MCSU724OS3 | M90C 7x24 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes verification of installation, inspection of UPS and commisioningof UPS by the Startup technician. On-site Warranty covers labor for corrective maintenance. | 6630
90001296 | MCPM58 | M90C Preventative Maintenance Service, 5x8. For Zone 1 (within 100 miles of XPC Service Center). | 3500
90001297 | MCPM724 | M90C Preventative Maintenance Service, 7x24. For Zone 1 (within 100 miles of XPC Service Center). | 4550
90000538 | SVCADD | Service adder for locations further than 100 miles. | 1050

## M90(L)U
|  | Return to Index | 2024-08-01
M90U and M90LU (Unity PF) Series Modular Double Conversion 3-Phase
Part Number | Model | Description | List Price
99000872 | M90-ENC (Unity PF) | Xtreme Power M90U (Unity PF) Series modular online 208/120 VAC three-phase UPS enclosure set up for internal battery. Includes 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; 2 Year Parts Warranty; Start-up and onsite labor is not included; 20.3" W x 39.4" D x 54.0" H. 474 lbs. Enclosure can accomodate up to 3 x 20k for 60KVA for 45KVA (or 3 x 15K for 45KVA) M90 (Unity PF) Power Modules and up to 12 M90 battery trays. Power modules and battery trays ordered seperately. | 14200
99000873 | M90L-ENC (Unity PF) | Xtreme Power M90U (Unity PF) Series modular online 208/120 VAC three-phase UPS enclosure set up for external battery (no internal batteries). Includes 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; 2 Year Parts Warranty; Start-up and onsite labor is not included; 20.3" W x 39.4" D x 30" H. 227 lbs. Enclosure can accomodate up to 3 x 20k for 60KVA (or 3 x 15K for 45KVA) M90U (Unity PF) Power Modules. Power modules and external battery ordered seperately. | 10300
99000870 | M90-PWRM (Unity PF) | Xtreme Power M90U Series 20kVA/20kW power module. 208/120 VAC three-phase; 19.5" W x 29.5" D x 5.5" H. 74 lbs. Unity PF | 8500
99000871 | M90-PWRM15 (Unity PF) | Xtreme Power M90U Series 15kVA/15kW power module. 208/120 VAC three-phase; 19.5" W x 29.5" D x 5.5" H. 73 lbs. Unity PF | 6700
90000563 | M90-BATT | Xtreme Power M90 battery tray for M90, M90U, M90-BOS. Includes (10) UPS 12580 batteries. Four (4) battery trays required for each 20kVA/18kW supported. __ Battery trays provide __ minutes runtime @ __KVA load. 2 year Warranty; 4,3" W x 28.5" D x 6.5" H; 68 lbs. | 890
90000885 | M90-BATT-EMPTY | Xtreme Power M90 empty battery tray for M90, M90U, M90-BOS. Includes battery interconnection cables. No batteries included. Minumum of four (4) battery trays required for each 20kVA/18kW supported. 4,3" W x 28.5" D x 6.5" H; 10 lbs. | 460
90000852 | M90-BOS | M90L Matching Battery Cabinet. Holds up to (12) M90-BATT battery trays. 20.3"W x 39.4"D x 30"H; 227 lbs. M90-BATT battery trays ordered seperately. | 5500
90000716 | M90-BC | External Modular Battery Cabinet. Holds up to 32 M90-BCBAT battery modules. 23.6"W x 43.8"D x 79.1"H; 416 lbs. Battery modules ordered seperately. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 12200
90000764 | M90-BCBAT | M90-BC Battery Module with (5)HR1290 batteries for M90-BC Battery Cabinet. 7.3"W x 38.5"D x 3.2"H; 85 lbs. Four modules required for each string. | 1025
90000851 | M90-BCBT | Empty Battery Tray for M90-BC External Battery Cabinet. 7.3"W x 38.5"D x 3.2"H; 14 lbs. Batteries ordered seperately. | 500
90000565 | M90 SKIRT | Xtreme Power M90(L) Skirt Kit. Installs between the UPS and floor to cover the casters and open space below UPS. Dims: TBD, 20 lbs. | 380
90000678 | M90-SEIS | Xtreme Power M90-ENC Seismic Anchor Kit. Includes Site Specific Seismic Calculations with State of California Engineer Stamp. Lead time 3-4 weeks ARO. Weight: 15 lbs. Requires site specific information to be submitted at time of order. One Kit required for each UPS. | 1900
| M90LU-SEIS | Xtreme Power M90L-ENC Seismic Anchor Kit. Includes Site Specific Seismic Calculations with State of California Engineer Stamp. Lead time 3-4 weeks ARO. Weight: 15 lbs. Requires site specific information to be submitted at time of order. One Kit required for each UPS . | 1900
| M90BC-SEIS | Xtreme Power M90-BC Seismic Anchor Kit. Includes Site Specific Seismic Calculations with State of California Engineer Stamp. Lead time 3-4 weeks ARO. Weight: 15 lbs. Requires site specific information to be submitted at time of order. One Kit required for each M90-BC battery cabinet. | 1900
M90 Bundles (with internal batteries)
Part Number | Model | Description | List Price
Bundle | M90U-15k04BM | Xtreme Power M90U Series 15KVA/15kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes one 15kVA/15kW power module; four (4) battery trays providing 9 minutes runtime at 15kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; 2 Year Parts Warranty; Start-up and onsite labor is not included; 20.3" W x 39.4" D x 54.0" H. 819 lbs. Enclosure can accommodate up to 2 additional 15k M90 (Unity PF) Power Modules and up to 8 additional M90 battery trays. | 24460
Bundle | M90U-15k06BM | Xtreme Power M90U Series 15KVA/15kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes one 15kVA/15kW power module; six (6) battery trays providing 16 minutes runtime at 15kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 955 lbs. Enclosure can accommodate up to 2 additional 15k M90 (Unity PF) Power Modules and up to 6 additional M90 battery trays. | 26240
Bundle | M90U-15k08BM | Xtreme Power M90U Series 15KVA/15kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes one 15kVA/15kW power module; eight (8) battery trays providing 22 minutes runtime at 15kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 1090 lbs. Enclosure can accommodate up to 2 additional 15k M90 (Unity PF)Power Modules and up to 4 additional M90 battery trays. | 28020
Bundle | M90U-15k10BM | Xtreme Power M90U Series 15KVA/15kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes one 15kVA/15kW power module; ten (10) battery trays providing 29 minutes runtime at 15kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 1225 lbs. Enclosure can accommodate up to 2 additional 15k M90 (Unity PF)Power Modules and up to 2 additional M90 battery trays. | 29800
Bundle | M90U-15k12BM | Xtreme Power M90U Series 15KVA/15kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes one 15kVA/15kW power module; twelve (12) battery trays providing 37 minutes runtime at 15kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 1361 lbs. Enclosure can accommodate up to 2 additional 15k M90 (Unity PF) Power Modules. | 31580
Bundle | M90U-20k04BM | Xtreme Power M90U Series 20KVA/20kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes one 20kVA/20kW power module; four (4) battery trays providing 6 minutes runtime at 20kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 820 lbs. Enclosure can accommodate up to 2 additional 20k M90 (Unity PF) Power Modules and up to 8 additional M90 battery trays. | 26260
Bundle | M90U-20k06BM | Xtreme Power M90U Series 20KVA/20kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes one 20kVA/20kW power module; x six (6) battery trays providing 11 minutes runtime at 20kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 956 lbs. Enclosure can accommodate up to 2 additional 20k M90 (Unity PF) Power Modules and up to 6 additional M90 battery trays. | 28040
Bundle | M90U-20k08BM | Xtreme Power M90U Series 20KVA/20kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes one 20kVA/20kW power module; eight (8) battery trays providing 16 minutes runtime at 20kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 1092 lbs. Enclosure can accommodate up to 2 additional 20k M90 (Unity PF) Power Modules and up to 4 additional M90 battery trays. | 29820
Bundle | M90U-20k10BM | Xtreme Power M90U Series 20KVA/20kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes one 20kVA/20kW power module; ten (10) battery trays providing 21 minutes runtime at 20kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 1228 lbs. Enclosure can accommodate up to 2 additional 20k M90 (Unity PF)Power Modules and up to 2 additional M90 battery trays. | 31600
Bundle | M90U-20k12BM | Xtreme Power M90U Series 20KVA/20kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes one 20kVA/20kW power module; twelve (12) battery trays providing 26 minutes runtime at 20kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Warranty; . 20.3" W x 39.4" D x 54.0" H. 1364 lbs. Enclosure can accommodate up to 2 additional 20k M90 (Unity PF) Power Modules. | 33380
Bundle | M90U-30k06BM | Xtreme Power M90U Series 30KVA/30kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes two 15kVA/15kW power modules; six (6) battery trays providing 6 minutes runtime at 30kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 1029 lbs. Enclosure can accommodate up to 1 additional 15k M90 (Unity PF)Power Module and up to 6 additional M90 battery trays. | 32940
Bundle | M90U-30k08BM | Xtreme Power M90U Series 30KVA/30kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes two 15kVA/15kW power modules; eight (8) battery trays providing 9 minutes runtime at 30kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 1165 lbs. Enclosure can accommodate up to 1 additional 15k M90 (Unity PF)Power Module and up to 4 additional M90 battery trays. | 34720
Bundle | M90U-30k10BM | Xtreme Power M90U Series 30KVA/30kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes two 15kVA/15kW power modules; ten (10) battery trays providing 12 minutes runtime at 30kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 1300 lbs. Enclosure can accommodate up to 1 additional 15k M90 (Unity PF) Power Module and up to 2 additional M90 battery trays. | 36500
Bundle | M90U-30k12BM | Xtreme Power M90U Series 30KVA/30kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes two 15kVA/15kW power modules; twelve (12) battery trays providing 16 minutes runtime at 30kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 1436 lbs. Enclosure can accommodate up to 1 additional 15k M90 (Unity PF) Power Module. | 38280
Bundle | M90U-40k08BM | Xtreme Power M90U Series 40KVA/40kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes two 20kVA/20kW power modules; eight (8) battery trays providing 6 minutes runtime at 40kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; . 20.3" W x 39.4" D x 54.0" H. 1166 lbs. Enclosure can accomodate 1 additional 20k M90 (Unity PF) Power Module and 4 additional battery trays. | 38320
Bundle | M90U-40k10BM | Xtreme Power M90U Series 40KVA/40kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes two 20kVA/20kW power modules; ten (10) battery trays providing 8 minutes runtime at 40kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; . 20.3" W x 39.4" D x 54.0" H. 1302 lbs. Enclosure can accomodate 1 additional 20k M90 (Unity PF) Power Module and 2 additional battery trays. | 40100
Bundle | M90U-40k12BM | Xtreme Power M90 Series 40KVA/40kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes two 20kVA/20kW power modules; twelve (12) battery trays providing 11 minutes runtime at 40kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; . 20.3" W x 39.4" D x 54.0" H. 1438 lbs. Enclosure can accommodate 1 additional 20k M90 (Unity PF) Power Module. | 41880
Bundle | M90U-45k08BM | Xtreme Power M90U Series 45KVA/45kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes three 15kVA/15kW power modules; eight (8) battery trays providing 5 minutes runtime at 45kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 1239 lbs. Enclosure can accommodate up to 4 additional M90 battery trays. | 41420
Bundle | M90U-45k10BM | Xtreme Power M90U Series 45KVA/45kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes three 15kVA/15kW power modules; ten (10) battery trays providing 7 minutes runtime at 45kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 1375 lbs. Enclosure can accommodate up to 2 additional M90 battery trays. | 43200
Bundle | M90U-45k12BM | Xtreme Power M90U Series 45KVA/45kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes three 15kVA/15kW power modules; twelve (12) battery trays providing 9 minutes runtime at 45kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 1511 lbs. | 44980
Bundle | M90U-60k10BM | Xtreme Power M90U Series 60KVA/60kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes three 20kVA/20kW power modules; ten (10) battery trays providing 4 minutes runtime at 60kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 1376 lbs. Enclosure can accommodate up to 2 additional M90 battery trays. | 48600
Bundle | M90U-60k12BM | Xtreme Power M90U Series 60KVA/60kW modular online 208/120 VAC three-phase UPS enclosure with internal battery. Includes three 20kVA/20kW power modules; twelve (12) battery trays providing 6 minutes runtime at 60kVA load; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 54.0" H. 1512 lbs. | 50380
M90L Bundles (for use with external batteries)
Part Number | Model | Description | List Price
Bundle | M90LU-15k | Xtreme Power M90LU Series 15KVA/15kW modular online 208/120 VAC three-phase UPS enclosure set up for external batteries. Includes one 15kVA/15kW power module; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 30.0" H. 300 lbs. Enclosure can accommodate up to 2 additional 15k M90 (Unity PF) Power Modules. | 17000
Bundle | M90LU-20k | Xtreme Power M90LU Series 20KVA/20kW modular online 208/120 VAC three-phase UPS enclosure set up for external batteries. Includes one 20kVA/20kW power module; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 30.0" H. 301 lbs. Enclosure can accommodate up to 2 additional 20k M90 (Unity PF) Power Modules. | 18800
Bundle | M90LU-30k | Xtreme Power M90LU Series 30KVA/30kW modular online 208/120 VAC three-phase UPS enclosure set up for external batteries. Includes two 15kVA/15kW power modules; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 30.0" H. 373 lbs. Enclosure can accommodate up to one additional 15k M90 (Unity PF) Power Module. | 23700
Bundle | M90LU-40k | Xtreme Power M90LU Series 40KVA/40kW modular online 208/120 VAC three-phase UPS enclosure set up for external batteries. Includes two 20kVA/20kW power modules; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 30.0" H. 375 lbs. Enclosure can accommodate up to one additional 20k M90 (Unity PF) Power Module. | 27300
Bundle | M90LU-45k | Xtreme Power M90LU Series 45KVA/45kW modular online 208/120 VAC three-phase UPS enclosure set up for external batteries. Includes three 15kVA/15kW power modules; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 30.0" H. 446 lbs. | 30400
Bundle | M90LU-60k | Xtreme Power M90 Series 60KVA/60kW modular online 208/120 VAC three-phase UPS enclosure set up for external batteries. Includes three 20kVA/20kW power modules; 5.7" LCD, static switch, and maintenance bypass switch ; 94% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCCA, RoHS; TAA Compliant; 2 Year Parts Warranty; Start-up and onsite labor is not included; . 20.3" W x 39.4" D x 30.0" H. 449 lbs. | 35800
External M90-BC Battery for use with M90L UPS
Part Number | Model | Description | List Price
Bundle | M90-BC-04B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (4) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 756 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 16300
Bundle | M90-BC-08B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (8) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 1096 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 20400
Bundle | M90-BC-12B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (12) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 1436 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 24500
Bundle | M90-BC-16B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (16) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 1776 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 28600
Bundle | M90-BC-20B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (20) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 2116 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 32700
Bundle | M90-BC-24B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (24) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 2456 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 36800
Bundle | M90-BC-28B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (28) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 2796 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 40900
Bundle | M90-BC-32B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (32) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Each battery string (4 modules) protected by a 100A breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 3136 lbs. Battery modules shipped on separate pallet. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 45000
External M90-BOS Battery for use with M90L UPS
Part Number | Model | Description | List Price
Bundle | M90-BOS-04B | M90L Matching Battery Cabinet with (4) M90-BATT battery trays. 20.3"W x 39.4"D x 30"H; 499 lbs. Can hold up to (8) additional M90-BATT battery trays. | 9060
Bundle | M90-BOS-06B | M90L Matching Battery Cabinet with (6) M90-BATT battery trays. 20.3"W x 39.4"D x 30"H; 635 lbs. Can hold up to (6) additional M90-BATT battery trays. | 10840
Bundle | M90-BOS-08B | M90L Matching Battery Cabinet with (8) M90-BATT battery trays. 20.3"W x 39.4"D x 30"H; 771 lbs. Can hold up to (4) additional M90-BATT battery trays. | 12620
Bundle | M90-BOS-10B | M90L Matching Battery Cabinet with (10) M90-BATT battery trays. 20.3"W x 39.4"D x 30"H; 907 lbs. Can hold up to (2) additional M90-BATT battery trays. | 14440
Bundle | M90-BOS-12B | M90L Matching Battery Cabinet with (12) M90-BATT battery trays. 20.3"W x 39.4"D x 30"H; 1043 lbs. | 16180
External Maintenance Bypass Options (wallmount)
Part Number | Model | Description | List Price
| 90885-C208310ECA060A06013MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 60 A, 10kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 22"W x 24"H x 9"D; 55 lbs. For Use with E91 15kVA and all M90 Family 15kVA UPS | Call For Price
| 90885-C208310ECA080A08013MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 60 A, 10kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 22"W x 24"H x 9"D; 55 lbs. For Use with E91 20kVA and all M90 Family 20kVA UPS | Call For Price
| 90880-C208322ECA125A12502MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 125 A, 22kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 30"W x 36"H x 10"D; 110 lbs. For Use with E91 30kVA and all M90 Family 30kVA UPS | Call For Price
| 90880-C208322ECA175A17502MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 175 A, 22kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 30"W x 36"H x 10"D; 110 lbs. For Use with all M90 Family up to 45kVA UPS | Call For Price
| 90881-C208365ECA250A25002MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 250 A, 65kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 30"W x 42"H x 11"D; 125 lbs. For Use with all M90 Family up to 60kVA | Call For Price
Note: | You can add 24V SKRU to 90880, 90881, and 90843 (not 90885) Series switches. You must replace the "02" in the P/N with "44" (example: 90880-C208322ECA150A15044MB, add SKRU adder to the list price, AND you must include a M90-COMM card to the UPS quote to interface with the MBP.
Contact XPC for MBS with distribution and/or transformer options.
Connectivity Options
Part Number | Model | Description | List Price
90000566 | SNMP-2P3 | Internal two port SNMP/WEB Card for use with E91, M90(U) and X90 Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-EMD Environmental Monitor; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 349
90000267 | MODBUS-IN | MODBUS CARD for use with the E91, M90(U) and X90 Series UPS; packaging = 7.25" x 6" x 2.5", 1 lbs | 319
90000398 | SNMP-EMD | Environmental Monitoring Sensor to monitor room temperature and humidity - used with SNMP-2P3 SNMP/WEB Card. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 180
90000498 | M90-COMM | Extra Communications card for M90. Allows for (6) programmable Form C relay contact outputs, (2) external Form C contact inputs, and up to (4) optional external temperature probe inputs and provides an additional card slot for Web/SNMP card . Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 370
| M90-BTS | Battery Temperature Sensor. Allows M90 and X90 Series UPS to monitor battery temperature and provide temperature compensated battery charging. A single temperature sensor can connect to temperature port on UPS chassis. Up to four additional temperature sensors can be connected with optional M90-COMM communication card. Temperature sensor has 3 meter cable. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 66
Service Options
Part Number | Model | Description | List Price
90000570 | M90SUS81 | M90, and M90L 5x8 Startup and 1 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes installation of the power modules and Internal battery trays, where applicable, by the Startup technician. | 4900
90000571 | M90SUS82 | M90, M90L, E90 and M90S 5x8 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes installation of the power modules and Internal battery trays, where applicable, by the Startup technician. | 5500
90000593 | M90SUS83 | M90, M90L, E90 and M90S 5x8 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes installation of the power modules and Internal battery trays, where applicable, by the Startup technician. | 8400
90000592 | M90SU7242 | M90, M90L, E90 and M90S 7x24 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes installation of the power modules and Internal battery trays, where applicable, by the Startup technician. | 7150
90000647 | M90SU7245 | M90, M90L, E90 and M90S Startup 7x24 and 5 year On-Site Warranty. For Zone 1 (within 100 miles of XPC Service Center). Does not include preventative maintenance visits. | 17900
90000594 | M90EXW1YR | M90, M90L, E90 and M90S One year extention of factory warranty. This warranty covers parts and depot repair labor. | 3200
90000648 | M90PM724 | M90, M90L, E90 and M90S Preventative Maintenance Service, 7x24. For Zone 1 (within 100 miles of XPC Service Center). | 4600
90000538 | SVCADD | Service adder for locations further than 100 miles. | 1050
90000730 | MSOS3BM | On-Site 3 Year Warranty for M90-BCBAT Battery Module. Three year coverage includes replacement parts and on-site corrective maintenance. Services are 5x8. Purchase one On-Site 3 Year Warranty Plan for each M90-BCBAT Battery Module. Startup with 3 year on-site must be purchased for the M90 UPS System. | 350

## M90U-80& 140
|  | Return to Index | 2024-08-01
M90U-80 and M90U-140 Series (Unity PF) Modular Double Conversion Three-Phase Detailed Price Sheet
M90U-80 Series Ala Carte Solutions
99000874 | M90-ENC80 (Unity PF) | Xtreme Power M90U-80 Series (Unity PF) modular online 208/120 VAC three-phase UPS enclosure set up for internal or external battery (no internal batteries). Includes 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch , hot swappable internal batteries; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS, Energy Star; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 657 lbs. Enclosure can accomodate up to 4 x 15kVA or 20kVA M90 (Unity PF)Power Modules for up to 80KVA capacity and up to 16 x M90-80BAT battery modules. Power modules, internal battery modules and external battery ordered separately. | 20000
99000870 | M90-140-ENC (Unity PF) | Xtreme Power M90-140 Series (Unity PF) modular online 208/120 VAC three-phase UPS enclosure set up for external battery (no internal batteries). Includes 10" LCD touch screen, front mounted front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 657 lbs. Enclosure can accomodate up to 8 x 20kVA or 15kVA M90 (Unity PF) Power Modules for maximum 140KVA N+1 capacity. Power modules and external battery ordered separately. | 26000
99000870 | M90-PWRM (Unity PF) | Xtreme Power M90U Series 20kVA/20kW power module. 208/120 VAC three-phase; 19.5" W x 29.5" D x 5.5" H. 74 lbs. Unity PF | 8500
99000871 | M90-PWRM15 (Unity PF) | Xtreme Power M90U Series 15kVA/15kW power module. 208/120 VAC three-phase; 19.5" W x 29.5" D x 5.5" H. 73 lbs. Unity PF | 6700
90000763 | M90-80BAT | Internal Battery Module for M90-80 UPS. Contains (10) CSB 12580 Batteries each, 2 battery modules required per string, must be purchased in multiplies of 2, (xx) battery modules will provide __ minutes runtime @ ___kW load, Dims: 4.3"W x 28.5"D x 6.5"H, Weight 70 lbs. | 990
90000716 | M90-BC | M90-80 and M90-140 Matching External Modular Battery Cabinet. Holds up to (32) x M90-BCBAT Battery Modules; 2 Year Warranty, Dims 23.6"W x 43.3"D x 79.1"H, Weight 416 lbs. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 12200
90000764 | M90-BCBAT | Battery Module for M90-BC External Battery Cabinet. Contains (5) CSB HR1290 Batteries each, 4 battery modules required per string, must be purchased in multiplies of 4, (xx) battery modules will provide ___ minutes runtime @ ___kW load, Dims: 7.3"W x 38.5"D x 3.2"H, Weight 85 lbs. | 1025
90000850 | M90-80BT | Empty Battery Tray for M90-80. Each tray can hold 10 x 12V, 9AH batteries per tray. Two trays required for a full string. Dims; 4.3"H x 28.5" D x 6.5" H, 15 lbs. Includes battery to battery cabling. Batteries ordered seperately. | 500
90000851 | M90-BCBT | Empty Battery Tray for M90-BC. Each Tray can hold 5 x 12V, 20AH batteries per tray. Four trays required for a full string. Dims; 7.3"H x 38.5" D x 3.2" H, 14 lbs. Includes battery to battery cabling. Batteries ordered seperately. | 525
90000767 | M90-BUS | Bus Bar Kit for paralleled M90-BC External Battery Cabinets. Dims: 20"W x 4"D x 2.5"H, Weight 9 lbs. | 500
90001213 | M90-CBL | Cable kit for connecting M90-BC battery cabinet to M90U-140 or M90U-80 UPS. Includes 8’ cables and lugs. Pricing for longer length cables is available upon request. Quantity 2 required for M90U-140 UPS Systems. | 1050
| M90U80-SEIS | Xtreme Power M90-ENC80 Seismic Anchor Kit. Includes Site Specific Seismic Calculations with State of California Engineer Stamp. Lead time 3-4 weeks ARO. Weight: 15 lbs. Requires site specific information to be submitted at time of order. One Kit required for each UPS . | 1900
| M90U140-SEIS | Xtreme Power M90-ENC140 Seismic Anchor Kit. Includes Site Specific Seismic Calculations with State of California Engineer Stamp. Lead time 3-4 weeks ARO. Weight: 15 lbs. Requires site specific information to be submitted at time of order. One Kit required for each UPS . | 1900
| M90BC-SEIS | Xtreme Power M90-BC Seismic Anchor Kit. Includes Site Specific Seismic Calculations with State of California Engineer Stamp. Lead time 3-4 weeks ARO. Weight: 15 lbs. Requires site specific information to be submitted at time of order. One Kit required for each M90-BC battery cabinet. | 1900
M90U-80 Series UPS Bundled Solutions with 20kVA Unity PF Power Modules
Part Number | Model | Description | List Price
Bundle | M90U80-20K00B | Xtreme Power M90U-80 Series bundle; 20KVA/20KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (1) Power Module, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch ; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 731 lbs. Enclosure can accomodate up to 4 x 20kVA M90 Power Modules for 80KVA capacity. Power module(s) shipped on separate pallet. Additional power modules and external battery ordered separately. | 28500
Bundle | M90U80-20K04B | Xtreme Power M90U-80 Series bundle; 20KVA/20KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (1) Power Module, (4) M90-80BAT Battery Modules providing 6 minutes runtime at 20KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch ; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1011 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 32460
Bundle | M90U80-20K06B | Xtreme Power M90U-80 Series bundle; 20KVA/20KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (1) Power Module, (6) M90U-80BAT Battery Modules providing 11 minutes runtime at 20KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch ; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1151 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 34440
Bundle | M90U80-20K08B | Xtreme Power M90U-80 Series bundle; 20KVA/20KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (1) Power Module, (8) M90-80BAT Battery Modules providing 16 minutes runtime at 20KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch ; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1291 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 36420
Bundle | M90U80-20K10B | Xtreme Power M90U-80 Series bundle; 20KVA/20KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (1) Power Module, (10) M90-80BAT Battery Modules providing 21 minutes runtime at 20KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch ; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1431 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 38400
Bundle | M90U80-20K12B | Xtreme Power M90U-80 Series bundle; 20KVA/20KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (1) Power Module, (12) M90-80BAT Battery Modules providing 26 minutes runtime at 20KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch ; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1571 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 40380
Bundle | M90U80-20K14B | Xtreme Power M90U-80 Series bundle; 20KVA/20KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (1) Power Module, (14) M90-80BAT Battery Modules providing 31 minutes runtime at 20KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch ; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1711 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 42360
Bundle | M90U80-20K16B | Xtreme Power M90U-80 Series bundle; 20KVA/20KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (1) Power Module, (16) M90-80BAT Battery Modules providing 37 minutes runtime at 20KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch ; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1851 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity. Power and battery modules shipped on separate pallet. Additional power modules ordered separately. | 44340
Bundle | M90U80-40K00B | Xtreme Power M90U-80 Series bundle; 40KVA/40KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (2) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch ; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 805 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity. Power module(s) shipped on separate pallet. Additional power modules and external battery ordered separately. | 37000
Bundle | M90U80-40K08B | Xtreme Power M90U-80 Series bundle; 40KVA/40KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (2) Power Modules, (8) M90-80BAT Battery Modules providing 6 minutes runtime at 40kW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1365 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 44920
Bundle | M90U80-40K10B | Xtreme Power M90U-80 Series bundle; 40KVA/40KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (2) Power Modules, (10) M90-80BAT Battery Modules providing 8 minutes runtime at 40kW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1505 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 46900
Bundle | M90U80-40K12B | Xtreme Power M90U-80 Series bundle; 40KVA/40KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (2) Power Modules, (12) M90U-80BAT Battery Modules providing 11 minutes runtime at 40kW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1645 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 48880
Bundle | M90U80-40K14B | Xtreme Power M90U-80 Series bundle; 40KVA/40KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (2) Power Modules, (14) M90-80BAT Battery Modules providing 13 minutes runtime at 40kW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1785 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 50860
Bundle | M90U80-40K16B | Xtreme Power M90U-80 Series bundle; 40KVA/40KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (2) Power Modules, (16) M90-80BAT Battery Modules providing 13 minutes runtime at 40kW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1925 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity. Power and battery modules shipped on separate pallet. Additional power modules ordered separately. | 52840
Bundle | M90U80-60K00B | Xtreme Power M90U-80 Series bundle; 60KVA/60KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (3) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 879 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity. Power module(s) shipped on separate pallet. Additional power modules and external battery ordered separately. | 45500
Bundle | M90U80-60K10B | Xtreme Power M90U-80 Series bundle; 60KVA/60KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (3) Power Modules, (10) M90-80BAT Battery Modules providing 4 minutes runtime at 60kW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1579 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity and up to 16 battery modules for longer runtime.. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 55400
Bundle | M90U80-60K12B | Xtreme Power M90U-80 Series bundle; 60KVA/60KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (3) Power Modules, (12) M90-80BAT Battery Modules providing 6 minutes runtime at 60kW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1719 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity and up to 16 battery modules for longer runtime.. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 57380
Bundle | M90U80-60K14B | Xtreme Power M90U-80 Series bundle; 60KVA/60KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (3) Power Modules, (14) M90-80BAT Battery Modules providing 8 minutes runtime at 60kW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1859 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity and up to 16 battery modules for longer runtime.. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 59360
Bundle | M90U80-60K16B | Xtreme Power M90U-80 Series bundle; 60KVA/60KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (3) Power Modules, (16) M90-80BAT Battery Modules providing 9 minutes runtime at 60kW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1999 lbs. Enclosure can accomodate up to 4 x 20kVA M90 (Unity PF) Power Modules for 80KVA capacity. Power and battery modules shipped on separate pallet. Additional power modules ordered separately. | 61340
Bundle | M90U80-80K00B | Xtreme Power M90U-80 Series bundle; 80KVA/80KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (4) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 953 lbs. Power module(s) shipped on separate pallet. External battery ordered separately. | 54000
Bundle | M90U80-80K14B | Xtreme Power M90U-80 Series bundle ; 80KVA/80KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (4) Power Modules, (14) M90-80BAT Battery Modules providing 4 minutes runtime at 80kW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1933 lbs. Enclosure can accomodate up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional battery modules ordered separately. | 67860
Bundle | M90U80-80K16B | Xtreme Power M90U-80 Series bundle ; 80KVA/80KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (4) Power Modules, (16) M90-80BAT Battery Modules providing 6 minutes runtime at 80kW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 2073 lbs. Power and battery modules shipped on separate pallet. | 69840
M90U-80 Series UPS Bundled Solutions W/ 15kVA Unity PF Power Modules
Bundle | M90U80-15k00B | Xtreme Power M90U-80 Series bundle; 15KVA/15KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (1) Power Module, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 730 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity. Power module(s) shipped on separate pallet. Additional power modules and external battery ordered separately. | 26700
Bundle | M90U80-15k04B | Xtreme Power M90U-80 Series bundle; 15KVA/15KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (1) Power Module, (4) M90-80BAT Battery Modules providing 9 minutes runtime at 15KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1010 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 30660
Bundle | M90U80-15k06B | Xtreme Power M90U-80 Series bundle; 15KVA/15KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (1) Power Module, (6) M90-80BAT Battery Modules providing 16 minutes runtime at 15KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1150 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 32640
Bundle | M90U80-15k08B | Xtreme Power M90U-80 Series bundle; 15KVA/15KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (1) Power Module, (8) M90-80BAT Battery Modules providing 22 minutes runtime at 15KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1290 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 34620
Bundle | M90U80-15k10B | Xtreme Power M90U-80 Series bundle; 15KVA/15KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (1) Power Module, (10) M90-80BAT Battery Modules providing 29 minutes runtime at 15KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1430 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 36600
Bundle | M90U80-15k12B | Xtreme Power M90U-80 Series bundle; 15KVA/15KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (1) Power Module, (12) M90-80BAT Battery Modules providing 37 minutes runtime at 15KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1570 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 38580
Bundle | M90U80-15k14B | Xtreme Power M90U-80 Series bundle; 15KVA/15KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (1) Power Module, (14) M90-80BAT Battery Modules providing 44 minutes runtime at 15KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1710 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 40560
Bundle | M90U80-15k16B | Xtreme Power M90U-80 Series bundle; 15KVA/15KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (1) Power Module, (16) M90-80BAT Battery Modules providing 52 minutes runtime at 15KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1850 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity. Power and battery modules shipped on separate pallet. Additional power modules ordered separately. | 42540
Bundle | M90U80-30k00B | Xtreme Power M90U-80 Series bundle; 30KVA/30KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (2) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 803 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity. Power module(s) shipped on separate pallet. Additional power modules and external battery ordered separately. | 33400
Bundle | M90U80-30k06B | Xtreme Power M90U-80 Series bundle; 30KVA/30KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (2) Power Modules, (6) M90-80BAT Battery Modules providing 6 minutes runtime at 30kW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1223 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 39340
Bundle | M90U80-30k08B | Xtreme Power M90U-80 Series bundle; 30KVA/30KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (2) Power Modules, (8) M90-80BAT Battery Modules providing 9 minutes runtime at 30KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1363 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 41320
Bundle | M90U80-30k10B | Xtreme Power M90U-80 Series bundle; 30KVA/30KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (2) Power Modules, (10) M90-80BAT Battery Modules providing 12 minutes runtime at 30KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1503 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 43300
Bundle | M90U80-30k12B | Xtreme Power M90U-80 Series bundle; 30KVA/30KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (2) Power Modules, (12) M90-80BAT Battery Modules providing 16 minutes runtime at 30KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1643 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 45280
Bundle | M90U80-30k14B | Xtreme Power M90U-80 Series bundle; 30KVA/30KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (2) Power Modules, (14) M90-80BAT Battery Modules providing 19 minutes runtime at 30KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1783 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 47260
Bundle | M90U80-30k16B | Xtreme Power M90U-80 Series bundle; 30KVA/30KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (2) Power Modules, (16) M90-80BAT Battery Modules providing 22 minutes runtime at 30KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1923 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity. Power and battery modules shipped on separate pallet. Additional power modules ordered separately. | 49240
Bundle | M90U80-45k00B | Xtreme Power M90U-80 Series bundle; 45KVA/45KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (3) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 876 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity. Power module(s) shipped on separate pallet. Additional power modules and external battery ordered separately. | 40100
Bundle | M90U80-45k08B | Xtreme Power M90U-80 Series bundle; 45KVA/45KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (3) Power Modules, (8) M90-80BAT Battery Modules providing 5 minutes runtime at 45KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1436 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 48020
Bundle | M90U80-45k10B | Xtreme Power M90U-80 Series bundle; 45KVA/45KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (3) Power Modules, (10) M90-80BAT Battery Modules providing 7 minutes runtime at 45KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1576 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 50000
Bundle | M90U80-45k12B | Xtreme Power M90U-80 Series bundle; 45KVA/45KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (3) Power Modules, (12) M90-80BAT Battery Modules providing 9 minutes runtime at 45KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1716 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 51980
Bundle | M90U80-45k14B | Xtreme Power M90U-80 Series bundle; 45KVA/45KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (3) Power Modules, (14) M90-80BAT Battery Modules providing 11 minutes runtime at 45KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1856 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity and up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional power and battery modules ordered separately. | 53960
Bundle | M90U80-45k16B | Xtreme Power M90U-80 Series bundle; 45KVA/45KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (3) Power Modules, (16) M90-80BAT Battery Modules providing 14 minutes runtime at 45KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1996 lbs. Enclosure can accomodate up to 4 x 15kVA M90 (Unity PF) Power Modules for 60KVA capacity. Power and battery modules shipped on separate pallet. Additional power modules ordered separately. | 55940
Bundle | M90U80-60Ka00B | Xtreme Power M90U-80 Series bundle; 60KVA/60KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (4) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 949 lbs. Power module(s) shipped on separate pallet. | 46800
Bundle | M90U80-60Ka10B | Xtreme Power M90U-80 Series bundle; 60KVA/60KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (4) Power Modules, (10) M90-80BAT Battery Modules providing 4 minutes runtime at 60KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1889 lbs. Enclosure can accomodate up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional battery modules ordered separately. | 56700
Bundle | M90U80-60Ka12B | Xtreme Power M90U-80 Series bundle; 60KVA/60KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (4) Power Modules, (12) M90-80BAT Battery Modules providing 6 minutes runtime at 60KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 2029 lbs. Enclosure can accomodate up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional battery modules ordered separately. | 58680
Bundle | M90U80-60Ka14B | Xtreme Power M90U-80 Series bundle; 60KVA/60KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (4) Power Modules, (14) M90-80BAT Battery Modules providing 8 minutes runtime at 60KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 2169 lbs. Enclosure can accomodate up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. Additional battery modules ordered separately. | 60660
Bundle | M90U80-60Ka16B | Xtreme Power M90U-80 Series bundle; 60KVA/60KW; Modular online 208/120 VAC three-phase UPS with internal battery. Includes (4) Power Modules, (16) M90-80BAT Battery Modules providing 9 minutes runtime at 60KW load, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 2309 lbs. Enclosure can accomodate up to 16 battery modules for longer runtime. Power and battery modules shipped on separate pallet. | 62640
M90U-140 Series UPS Bundled Solutions with 20kVA Unity PF Power Modules (no batteries)
Part Number | Model | Description | List Price
Bundle | M90U140-20K | Xtreme Power M90-140 Series bundle; 20KVA/20KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (1) Power Module, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 731 lbs. Enclosure can accomodate up to 8 x 20kVA M90 (Unity PF) Power Modules for 140KVA N+1 capacity. Power module(s) shipped on separate pallet. Additional power modules and external battery ordered separately. | 34500
Bundle | M90U140-40K | Xtreme Power M90-140 Series bundle; 40KVA/40KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (2) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 805 lbs. Enclosure can accomodate up to 8 x 20kVA M90 (Unity PF) Power Modules for 140KVA N+1 capacity. Power Modules shipped on separate pallet. Additional power modules and external battery ordered separately. | 43000
Bundle | M90U140-60K | Xtreme Power M90-140 Series bundle; 60KVA/60KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (3) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 879 lbs. Enclosure can accomodate up to 8 x 20kVA M90 (Unity PF) Power Modules for 140KVA N+1 capacity. Power Modules shipped on separate pallet. Additional power modules and external battery ordered separately. | 51500
Bundle | M90U140-80K | Xtreme Power M90-140 Series bundle; 80KVA/80KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (4) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 953 lbs. Enclosure can accomodate up to 8 x 20kVA M90 (Unity PF) Power Modules for 140KVA N+1 capacity. Power Modules shipped on separate pallet. Additional power modules and external battery ordered separately. | 60000
Bundle | M90U140-100K | Xtreme Power M90-140 Series bundle; 100KVA/100KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (5) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1027 lbs. Enclosure can accomodate up to 8 x 20kVA M90 (Unity PF) Power Modules for 140KVA N+1 capacity. Power Modules shipped on separate pallet. Additional power modules and external battery ordered separately. | 68500
Bundle | M90U140-120K | Xtreme Power M90-140 Series bundle; 120KVA/120KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (6) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1101 lbs. Enclosure can accomodate up to 8 x 20kVA M90 (Unity PF) Power Modules for 140KVA N+1 capacity. Power Modules shipped on separate pallet. Additional power modules and external battery ordered separately. | 77000
Bundle | M90U140-140K | Xtreme Power M90-140 Series bundle; 140KVA/140KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (7) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1175 lbs. Enclosure can accomodate up to 8 x 20kVA M90 (Unity PF) Power Modules for 140KVA N+1 capacity. Power Modules shipped on separate pallet. Additional power modules and external battery ordered separately. | 85500
Bundle | M90U140-140KN1 | Xtreme Power M90-140 Series bundle; 140KVA/140KW (N+1); Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (8) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1249 lbs. Power Modules shipped on separate pallet. External battery ordered separately. | 94000
M90U-140 Series UPS Bundled Solutions with 15kVA Unity PF Power Modules (no batteries)
Part Number | Model | Description | List Price
Bundle | M90U140-15K | Xtreme Power M90-140 Series bundle; 15KVA/15KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (1) Power Module, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 730 lbs. Enclosure can accomodate up to 8 x 15kVA M90 (Unity PF) Power Modules for 105KVA N+1 capacity. Power module(s) shipped on separate pallet. Additional power modules and external battery ordered separately. | 32700
Bundle | M90U140-30K | Xtreme Power M90-140 Series bundle; 30KVA/30KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (2) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 803 lbs. Enclosure can accomodate up to 8 x 15kVA M90 (Unity PF) Power Modules for 105KVA N+1 capacity. Power Modules shipped on separate pallet. Additional power modules and external battery ordered separately. | 39400
Bundle | M90U140-45K | Xtreme Power M90-140 Series bundle; 45KVA/45KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (3) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 876 lbs. Enclosure can accomodate up to 8 x 15kVA M90 (Unity PF) Power Modules for 105KVA N+1 capacity. Power Modules shipped on separate pallet. Additional power modules and external battery ordered separately. | 46100
Bundle | M90U140-60Ka | Xtreme Power M90-140 Series bundle; 60KVA/60KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (4) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 949 lbs. Enclosure can accomodate up to 8 x 15kVA M90 (Unity PF) Power Modules for 105KVA N+1 capacity. Power Modules shipped on separate pallet. Additional power modules and external battery ordered separately. | 52800
Bundle | M90U140-75K | Xtreme Power M90-140 Series bundle;75KVA/75KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (5) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1022 lbs. Enclosure can accomodate up to 8 x 15kVA M90 (Unity PF) Power Modules for 105KVA N+1 capacity. Power Modules shipped on separate pallet. Additional power modules and external battery ordered separately. | 59500
Bundle | M90U140-90K | Xtreme Power M90-140 Series bundle; 90KVA/90KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (6) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1095 lbs. Enclosure can accomodate up to 8 x 15kVA M90 (Unity PF) Power Modules for 105KVA N+1 capacity. Power Modules shipped on separate pallet. Additional power modules and external battery ordered separately. | 66200
Bundle | M90U140-105K | Xtreme Power M90-140 Series bundle; 105KVA/105KW; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (7) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1169 lbs. Enclosure can accomodate up to 8 x 15kVA M90 (Unity PF) Power Modules for 105KVA N+1 capacity. Power Modules shipped on separate pallet. Additional power modules and external battery ordered separately. | 72900
Bundle | M90U140-105KN1 | Xtreme Power M90-140 Series bundle; 105KVA/105KW N+1; Modular online 208/120 VAC three-phase UPS set up for external battery (no internal batteries). Includes (7) Power Modules, 10" LCD touch screen, front mounted maintenance bypass with static switch interlock, modular static switch; up to 94.1% efficiency in online mode or 98% efficiency in ECO mode; communication port; UL-1778 (TUV), cUL, FCC A, RoHS; TAA Compliant ; 2 Year Parts Warranty; Start-up and onsite labor is not included; 23.6"W x 43.3"D x 79.1"H; 1242 lbs. Power Modules shipped on separate pallet. External battery ordered separately. | 79600
M90-BC Modular Battery Cabinet Bundles
Part Number | Model | Description | List Price
Bundle | M90-BC-04B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (4) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 756 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 16300
Bundle | M90-BC-08B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (8) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 1096 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 20400
Bundle | M90-BC-12B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (12) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 1436 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 24500
Bundle | M90-BC-16B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (16) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 1776 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 28600
Bundle | M90-BC-20B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (20) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 2116 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 32700
Bundle | M90-BC-24B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (24) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 2456 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 36800
Bundle | M90-BC-28B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (28) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accomodate up to 32 battery modules for longer runtime. Battery modules must be added in sets of four. Each battery string (4 modules) protected by a 100A breaker.Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 2796 lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 40900
Bundle | M90-BC-32B | Xtreme Power M90-BC Modular Battery Cabinet bundle. Includes M90-BC Battery Cabinet and (32) M90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Each battery string (4 modules) protected by a 100A breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 43.3"D x 79.1"H; 3136 lbs. Battery modules shipped on separate pallet. Up to 2 battery cabinets can be paralleled with M90-BUS option. Battery Cabinet to UPS Cable not included. Optional M90-CBL - Battery Cabinet to M9080 or M90140 Cable Available. | 45000
External Maintenance Bypass Options
Part Number | Model | Description | List Price
| 90881-C208365ECA250A25002MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 250 A, 65kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 30"W x 42"H x 11"D; 125 lbs. For Use with all M90 Family up to 60kVA | Call For Price
| 90881-C208365ECA300A30002MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 300 A, 65kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 30"W x 42"H x 11"D; 125 lbs. For Use with all M90 Family up to 75kVA | Call For Price
| 90881-C208365ECA350A35002MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 350 A, 65kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 30"W x 42"H x 11"D; 125 lbs. For Use with all M90 Family up to 80kVA | Call For Price
| 90881-C208365ECA400A40002MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 400 A, 65kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 30"W x 42"H x 11"D; 125 lbs. For Use with all M90 Family up to 105kVA | Call For Price
| 90882-C208365ECA500A50002MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 500 A, 65kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 36"W x 48"H x 13.5"D; 165 lbs. For Use with all M90 Family up to 120kVA | Call For Price
| 90882-C208365ECA600A60002MB | Three-Breaker Maintenance Bypass Switch; 208VAC, 600 A, 65kAIC; Wallmount; includes Bypass Input Breaker, Maintenance Isolation Breaker, and Maintenance Bypass Breaker, kirk-key locks, lockable front panel. 36"W x 48"H x 13.5"D; 165 lbs. For Use with all M90 Family up to 140kVA | Call For Price
Contact XPC for MBS with distribution and/or transformer options.
Connectivity Options
Part Number | Model | Description | List Price
90000566 | SNMP-2P3 | Internal two port SNMP/WEB Card for use with E91, M90(U) and X90 Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-EMD Environmental Monitor; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 349
90000267 | MODBUS-IN | MODBUS CARD for use with the E91, M90(U) and X90 Series UPS; packaging = 7.25" x 6" x 2.5", 1 lbs | 319
90000398 | SNMP-EMD | Environmental Monitoring Sensor to monitor room temperature and humidity - used with SNMP-2P3 SNMP/WEB Card. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 180
90000498 | M90-COMM | Extra Communications card for M90. Allows for (6) programmable Form C relay contact outputs, (2) external Form C contact inputs, and up to (4) optional external temperature probe inputs and provides an additional card slot for Web/SNMP card . Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 370
| M90-BTS | Battery Temperature Sensor. Allows M90 and X90 Series UPS to monitor battery temperature and provide temperature compensated battery charging. A single temperature sensor can connect to temperature port on UPS chassis. Up to four additional temperature sensors can be connected with optional M90-COMM communication card. Temperature sensor has 3 meter cable. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 66
Service Options
Part Number | Model | Description | List Price
90000768 | M90814SU581 | M90-80 and M90-140 5x8 Startup and 1 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center) StartUP includes installation of the M90 power modules and Internal battery trays by the startup technician. | 5900
90000769 | M90814SU582 | M90-80 and M90-140 5x8 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes installation of the M90 power modules and Internal battery trays by the startup technician. | 6500
90000770 | M90814SU583 | M90-80 and M90-140 5x8 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes installation of the M90 power modules and Internal battery trays by the startup technician. | 9600
90000772 | M90814SU72 | M90-80 and M90-140 7x24 Startup and 2 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes installation of the M90 power modules and Internal battery trays by the startup technician. | 8450
90000773 | M90814SU73 | M90-80 and M90-140 7x24 Startup and 3 year on-site warranty. For Zone 1 (within 100 miles of XPC Service Center). StartUP includes installation of the M90 power modules and Internal battery trays by the startup technician. | 11700
90000774 | M90814EX1 | M90-80 and M90-140 One year extention of factory warranty. This warranty covers parts and depot repair labor, extending standard factory warranty to 3yrs. | 4200
90000775 | M90814PM7 | M90-80 and M90-140 Preventative Maintenance Service, 7x24. For Zone 1 (within 100 miles of XPC Service Center). | 4900
90000730 | MSOS3BM | On-Site 3 Year Warranty for M90-BCBAT Battery Module. Three year coverage includes replacement parts and on-site corrective maintenance. Services are 5x8. Purchase one On-Site 3 Year Warranty Plan for each M90-BCBAT Battery Module. Startup with 3 year on-site must be purchased for the M90 UPS System. | 350
90000538 | SVCADD | Service adder for locations further than 100 miles. | 1050

## X90-1S & 2S
|  | Return to Index | 2025-11-01
X90 1-Slot & 2-Slot 50-140kVA
X90-1S & 2S Series Ala Carte Solutions
Part Number | Model | Description | List Price
90001316 | X90-ENC1S | X90-1S Series (Unity PF) modular online 480VAC three-phase, 3-wire top entry UPS enclosure set up for internal and/or external battery (no internal batteries included). Includes 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 58"H; 357 lbs. Enclosure can accommodate 1 x 50kVA/kW or 70kVA/kW X90 Power Modules for up to 70KVA/kW capacity and up to 16 x X90-BCBAT battery modules. Power module, internal battery modules and external battery ordered separately. | 29200
90001013 | X90-ENC2S | X90-2S Series (Unity PF) modular online 480VAC three-phase, 3-wire top entry UPS enclosure set up for internal and/or external battery (no internal batteries included). Includes 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 79"H; 657 lbs. Enclosure can accommodate up to 2 x 50kVA/kW or 70kVA/kW X90 Power Modules for up to 140KVA/kW capacity and up to 20 x X90-BCBAT battery modules. Power modules, internal battery modules and external battery ordered separately. | 35700
90001016 | X90-2SPM50 | Xtreme Power X90 50kVA/50kW power module. 480 VAC three-phase; 19.5" W x 29.5" D x 5.5" H. 104 lbs. | 9600
90001017 | X90-2SPM70 | Xtreme Power X90 Series 70kVA/70kW power module. 208/120 VAC three-phase; 19.5" W x 29.5" D x 5.5" H. 105 lbs. | 10500
90001066 | X90-BC | X90 Matching External Modular Battery Cabinet. Holds up to (36) x X90-BCBAT Battery Modules; 2 Year Warranty, Dims 23.6"W x 42"D x 79"H, Weight 416 lbs. | 6500
90001067 | X90-BCBAT | Battery Module for X90-2S Internal or X90-BC External Battery Cabinet. Contains (10) CSB 12580 Batteries each, 4 battery modules required per string, must be purchased in multiplies of 4, (xx) battery modules will provide ___ minutes runtime @ ___kW load, Dims: 4.3"W x 28.5"D x 6.5"H, Weight 70 lbs. | 1090
90001076 | X90-BCBT | Empty Battery Tray for X90-2S or X90-BC. Each Tray can hold (10) CSB 12580 batteries per tray. Four trays required for a full string. Dims; 4.3"W x 28.5"D x 6.5"H, 15 lbs. Includes battery to battery cabling. Batteries ordered separately. | 500
90001071 | X90-SC2S | Side car for bottom entry. Dims: 6.1"W x 42"D x 79"H | 900
90001075 | X90-SEIS | Xtreme Power X90-2S Seismic Anchor Kit. Includes Site Specific Seismic Calculations with State of California Engineer Stamp. Lead time 3-4 weeks ARO. Weight: TBD lbs. Requires site specific information to be submitted at time of order. One Kit required for each X90-2S UPS. | 1900
| X90BC-SEIS | Xtreme Power X90-BC Seismic Anchor Kit. Includes Site Specific Seismic Calculations with State of California Engineer Stamp. Lead time 3-4 weeks ARO. Weight: TBD lbs. Requires site specific information to be submitted at time of order. One Kit required for each X90-BC battery cabinet. | 1900
X90-1S Series UPS Bundled Solutions with 50kVA Unity PF Power Modules
Part Number | Model | Description | List Price
Bundle | X901S-50K00B | Xtreme Power X90-1S Series bundle; 50KVA/50KW; Modular online 480VAC three-phase, 3-Wire top entry UPS set up for external battery (no internal batteries). Includes (1) Power Module, static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 58"H; 461 lbs. Enclosure can accommodate 1 x 50kVA/kW or 70kVA/kW X90 Power Modules for up to 70KVA/kW capacity and up to 16 x X90-BCBAT battery modules External battery ordered separately. Power Module ships on a separate pallet. | 38800
Bundle | X901S-50K12B | Xtreme Power X90-1S Series bundle; 50KVA/50KW; Modular online 480VAC three-phase, 3-Wire top entry UPS. Includes (1) Power Module, (12) X90-BCBAT providing approximately 7 minutes at 50kW load; static switch,10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 58"H; 1301 lbs. Enclosure can accommodate 1 x 50kVA/kW or 70kVA/kW X90 Power Modules for up to 70KVA/kW capacity and up to 16 x X90-BCBAT battery modules Power and Battery Modules ship on a separate pallet. | 51880
Bundle | X901S-50K16B | Xtreme Power X90-1S Series bundle; 50KVA/50KW; Modular online 480VAC three-phase, 3-Wire top entry UPS. Includes (1) Power Module, (16) X90-BCBAT providing approximately 11 minutes at 50kW load, static switch; 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 58"H; 1581 lbs. Enclosure can accommodate 1 x 50kVA/kW or 70kVA/kW X90 Power Modules for up to 70KVA/kW capacity and up to 16 x X90-BCBAT battery modules. Power and Battery Modules ship on a separate pallet. | 56240
X90-1S Series UPS Bundled Solutions with 70kVA Unity PF Power Modules
Part Number | Model | Description | List Price
Bundle | X901S-70k00B | Xtreme Power X90-1S Series bundle; 70KVA/70KW; Modular online 480VAC three-phase, 3-Wire top entry UPS set up for external battery (no internal batteries). Includes (1) Power Module, static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 58"H; 462 lbs. Enclosure can accommodate 1 x 50kVA/kW or 70kVA/kW X90 Power Modules for up to 70KVA/kW capacity and up to 16 x X90-BCBAT battery modules. Internal battery modules and external battery ordered separately. Power Module ships on a separate pallet. | 39700
Bundle | X901S-70k16B | Xtreme Power X90-1S Series bundle; 70KVA/70KW; Modular online 480VAC three-phase, 3-Wire top entry UPS. Includes (1) Power Module, (16) X90-BCBAT providing approximately 7 minutes at 70kW load; static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty is included; 23.6"W x 42"D x 58"H; 1582 lbs. Enclosure can accommodate 1 x 50kVA/kW or 70kVA/kW X90 Power Modules for up to 70KVA/kW capacity and up to 16 x X90-BCBAT battery modules. Power and Battery Modules ship on a separate pallet. | 57140
X90-2S Series UPS Bundled Solutions with 50kVA Unity PF Power Modules
Part Number | Model | Description | List Price
Bundle | X902S-50K00B | Xtreme Power X90-2S Series bundle; 50KVA/50KW; Modular online 480VAC three-phase, 3-Wire top entry UPS set up for external battery (no internal batteries). Includes (1) Power Module, static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 79"H; 761 lbs. Enclosure can accommodate up to 2 x 50kVA/kW X90 Power Modules for up to 100KVA/kW capacity and up to 20 x X90-BCBAT battery modules. External battery ordered separately. Power Modules ship on a separate pallet. | 45300
Bundle | X902S-50K12B | Xtreme Power X90-2S Series bundle; 50KVA/50KW; Modular online 480VAC three-phase, 3-Wire top entry UPS. Includes (1) Power Module, (12) X90-BCBAT providing approximately 8 minutes at 50kW load; static switch,10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 79"H; 1601 lbs. Enclosure can accommodate up to 2 x 50kVA/kW X90 Power Modules for up to 100KVA/kW capacity and up to 20 x X90-BCBAT battery modules. Power and Battery Modules ship on a separate pallet. | 28380
Bundle | X902S-50K16B | Xtreme Power X90-2S Series bundle; 50KVA/50KW; Modular online 480VAC three-phase, 3-Wire top entry UPS. Includes (1) Power Module, (16) X90-BCBAT providing approximately 12 minutes at 50kW load, static switch; 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 79"H; 1881 lbs. Enclosure can accommodate up to 2 x 50kVA/kW X90 Power Modules for up to 100KVA/kW capacity and up to 20 x X90-BCBAT battery modules. Power and Battery Modules ship on a separate pallet. | 62740
Bundle | X902S-50K20B | Xtreme Power X90-2S Series bundle; 50KVA/50KW; Modular online 480VAC three-phase, 3-Wire top entry UPS. Includes (1) Power Module, (20) X90-BCBAT providing approximately 16 minutes at 50kW load; static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 79"H; 2161 lbs. Enclosure can accommodate up to 2 x 50kVA/kW X90 Power Modules for up to 100KVA/kW capacity and up to 20 x X90-BCBAT battery modules. Power and Battery Modules ship on a separate pallet. | 67100
Bundle | X902S-100K00B | Xtreme Power X90-2S Series bundle; 100KVA/100KW; Modular online 480VAC three-phase, 3-Wire top entry UPS set up for external battery (no internal batteries). Includes (2) Power Modules, static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 79"H; 865 lbs. Enclosure can accommodate up to 20 x X90-BCBAT battery modules. External battery cabinet ordered separately. Power Modules ship on a separate pallet. | 54900
Bundle | X902S-100K20B | Xtreme Power X90-2S Series bundle; 100KVA/100KW; Modular online 480VAC three-phase, 3-Wire top entry UPS. Includes (2) Power Module, (20) X90-BCBAT providing approximately 6 minutes at 100kW load; static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 79"H; 2265 lbs. Power and Battery Modules ship on a separate pallet. | 76700
X90-2S Series UPS Bundled Solutions W/ 70kVA Unity PF Power Modules
Bundle | X902S-70k00B | Xtreme Power X90-2S Series bundle; 70KVA/70KW; Modular online 480VAC three-phase, 3-Wire top entry UPS set up for external battery (no internal batteries). Includes (1) Power Module, static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 79"H; 762 lbs. Enclosure can accommodate up to 2 x 70kVA/kW X90 Power Modules for up to 140KVA/kW capacity and up to 20 x X90-BCBAT battery modules. External battery ordered separately. Power Modules ship on a separate pallet. | 46200
Bundle | X902S-70k16B | Xtreme Power X90-2S Series bundle; 70KVA/70KW; Modular online 480VAC three-phase, 3-Wire top entry UPS. Includes (1) Power Module, (16) X90-BCBAT providing approximately 8 minutes at 70kW load; static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty is included; 23.6"W x 42"D x 79"H; 1882 lbs. Enclosure can accommodate up to 2 x 70kVA/kW X90 Power Modules for up to 140KVA/kW capacity and up to 20 x X90-BCBAT battery modules. Power and Battery Modules ship on a separate pallet. | 63640
Bundle | X902S-70k20B | Xtreme Power X90-2S Series bundle; 70KVA/70KW; Modular online 480VAC three-phase, 3-Wire top entry UPS. Includes (1) Power Module, (20) X90-BCBAT providing approximately 10 minutes at 70kW load; static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 79"H; 2162 lbs. Enclosure can accommodate up to 2 x 70kVA/kW X90 Power Modules for up to 140KVA/kW capacity and up to 20 x X90-BCBAT battery modules. Power and Battery Modules ship on a separate pallet. | 68000
Bundle | X902S-140k00B | Xtreme Power X90-2S Series bundle; 140KVA/140KW; Modular online 480VAC three-phase, 3-Wire top entry UPS set up for external battery (no internal batteries). Includes (2) Power Modules, static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; 23.6"W x 42"D x 79"H; 867 lbs. Enclosure can accommodate up to 20 x X90-BCBAT battery modules. External battery cabinet ordered separately. Power Modules ship on a separate pallet. | 56700
Bundle | X902S-140k28B | Xtreme Power X90-2S Series bundle; 140KVA/140KW; Modular online 480VAC three-phase, 3-Wire top entry UPS. Includes (2) Power Modules, X90-BC with (28) X90-BCBAT providing approximately 6 minutes at 140kW load; static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; UPS and Battery cabinet each 23.6"W x 42"D x 79"H; UPS 867lbs, X90-BC 2376lbs. Power and Battery Modules ship on a separate pallet. Qty 28 open battery slots for runtime expansion. | 93720
Bundle | X902S-140k36B | Xtreme Power X90-2S Series bundle; 140KVA/140KW; Modular online 480VAC three-phase, 3-Wire top entry UPS. Includes (2) Power Modules, X90-BC, (36) X90-BCBAT providing approximately 8 minutes at 140kW load; static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; UPS and Battery cabinet each 23.6"W x 42"D x 79"H; UPS 867 lbs, X90-BC 2936 lbs. Power and Battery Modules ship on a separate pallet. Qty 20 open battery slots for runtime expansion. | 102440
Bundle | X902S-140k40B | Xtreme Power X90-2S Series bundle; 140KVA/140KW; Modular online 480VAC three-phase, 3-Wire top entry UPS. Includes (2) Power Modules, X90-BC, (40) X90-BCBAT providing approximately 10 minutes at 140kW load; static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; UPS and Battery cabinet each 23.6"W x 42"D x 79"H; UPS 1147 lbs, X90-BC 2936 lbs. Power and Battery Modules ship on a separate pallet. Qty 16 open battery slots for runtime expansion. | 106880
Bundle | X902S-140k48B | Xtreme Power X90-2S Series bundle; 140KVA/140KW; Modular online 480VAC three-phase, 3-Wire top entry UPS. Includes (2) Power Modules, X90-BC, (48) X90-BCBAT providing approximately 12 minutes at 140kW load; static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; UPS and Battery cabinet each 23.6"W x 42"D x 79"H; UPS 1707 lbs, X90-BC 2936 lbs. Power and Battery Modules ship on a separate pallet. Qty 8 open battery slots for runtime expansion. | 115520
Bundle | X902S-140k56B | Xtreme Power X90-2S Series bundle; 140KVA/140KW; Modular online 480VAC three-phase, 3-Wire top entry UPS. Includes (2) Power Modules, X90-BC, (56) X90-BCBAT providing approximately 15 minutes at 140kW load; static switch, 10" LCD touch screen, front mounted 65kAIC maintenance bypass with static switch interlock, hot swappable internal batteries; up to 96.5% efficiency in online mode or 99% efficiency in ECO mode; communication port; UL-1778, cUL, FCC A, RoHS, TAA Compliant ; Start-up (5x8) and 2-Year on-site warranty are included; UPS and Battery cabinet each 23.6"W x 42"D x 79"H; UPS 2265 7lbs, X90-BC 2936 lbs. Power and Battery Modules ship on a separate pallet. | 124240
X90-BC Modular Battery Cabinet Bundles
Part Number | Model | Description | List Price
Bundle | X90BC-04B | Xtreme Power X90-BC Modular Battery Cabinet bundle. Includes X90-BC Battery Cabinet and (4) X90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accommodate up to 36 battery modules for longer runtime. Battery modules must be added in sets of four. Battery Cabinet protected by a breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 42"D x 79"H; 696lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled. | 10860
Bundle | X90BC-08B | Xtreme Power X90-BC Modular Battery Cabinet bundle. Includes X90-BC Battery Cabinet and (8) X90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accommodate up to 36 battery modules for longer runtime. Battery modules must be added in sets of four. Battery Cabinet protected by a breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 42"D x 79"H; 976lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled. | 15220
Bundle | X90BC-12B | Xtreme Power X90-BC Modular Battery Cabinet bundle. Includes X90-BC Battery Cabinet and (12) X90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accommodate up to 36 battery modules for longer runtime. Battery modules must be added in sets of four. Battery Cabinet protected by a breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 42"D x 79"H; 1256lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled. | 19580
Bundle | X90BC-16B | Xtreme Power X90-BC Modular Battery Cabinet bundle. Includes X90-BC Battery Cabinet and (16) X90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accommodate up to 36 battery modules for longer runtime. Battery modules must be added in sets of four. Battery Cabinet protected by a breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ;23.6"W x 42"D x 79"H; 1536lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled. | 23940
Bundle | X90BC-20B | Xtreme Power X90-BC Modular Battery Cabinet bundle. Includes X90-BC Battery Cabinet and (20) X90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accommodate up to 36 battery modules for longer runtime. Battery modules must be added in sets of four. Battery Cabinet protected by a breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 42"D x 79"H; 1816lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled. | 28300
Bundle | X90BC-24B | Xtreme Power X90-BC Modular Battery Cabinet bundle. Includes X90-BC Battery Cabinet and (24) X90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accommodate up to 36 battery modules for longer runtime. Battery modules must be added in sets of four. Battery Cabinet protected by a breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 42"D x 79"H; 2096lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled. | 32660
Bundle | X90BC-28B | Xtreme Power X90-BC Modular Battery Cabinet bundle. Includes X90-BC Battery Cabinet and (28) X90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accommodate up to 36 battery modules for longer runtime. Battery modules must be added in sets of four. Battery Cabinet protected by a breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 42"D x 79"H; 2376lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled. | 37020
Bundle | X90BC-32B | Xtreme Power X90-BC Modular Battery Cabinet bundle. Includes X90-BC Battery Cabinet and (32) X90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Enclosure can accommodate up to 36 battery modules for longer runtime. Battery modules must be added in sets of four. Battery Cabinet protected by a breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 42"D x 79"H; 2656lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled. | 41380
Bundle | X90BC-36B | Xtreme Power X90-BC Modular Battery Cabinet bundle. Includes X90-BC Battery Cabinet and (36) X90-BCBAT Battery Modules providing __ minutes runtime at __kW load. Battery modules must be added in sets of four. Battery Cabinet protected by a breaker. Two Year Parts Warranty; UL-1778 (TUV), cUL, FCC A, RoHS, TAA Compliant ; 23.6"W x 42"D x 79"H; 2936lbs. Battery modules shipped on separate pallet. Additional battery modules ordered separately. Up to 2 battery cabinets can be paralleled. | 45740
Connectivity Options
Part Number | Model | Description | List Price
90001245 | SNMP-2PG1 | Internal two port SNMP/WEB Card for use with X90, M90C, M90, M90L E91, and M90S Series UPS; Allows for monitoring and management of UPS through a web browser or SNMP platform: Provides shutdown of remote clients via LAN, and Email Notification of UPS status and events. Compatible with SNMP-TMPH temperature and humidity probe; Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 715
90000267 | MODBUS-IN | MODBUS CARD for use with the E91, M90(U) and X90 Series UPS; packaging = 7.25" x 6" x 2.5", 1 lbs | 319
90000398 | SNMP-TMPH | Temperature and humidity Probe - used with SNMP-2PG1 SNMP/WEB Card. Packaging = 7.25"W x 6.0"D x 2.5"H, 1.0 lbs | 329
| M90-BTS | Battery Temperature Sensor. Allows M90 and X90 Series UPS to monitor battery temperature and provide temperature compensated battery charging. A single temperature sensor can connect to temperature port on UPS chassis. Up to four additional temperature sensors can be connected with optional M90-COMM communication card. Temperature sensor has 3 meter cable. Packaging = 5.7"W x 5.2"D x 1.7"H, 0.3 lbs | 66
Service Options
Part Number | Model | Description | List Price
90001248 | X902SSU583 | Upgrade standard warranty to 3 years. Includes (1) PM (5x8) to be performed at beginning of year three. Must be purchased concurrently with equipment. Zone 1 - within 100 miles of XPC Service Center. | 6500
90001249 | X902SSU72 | Upgrade standard warranty to include 7x24 coverage. Must be purchased concurrently with equipment. Zone 1 - within 100 miles of XPC Service Center. | 2800
90001250 | X902SSU73 | Upgrade standard warranty to 3 years and 7x24 coverage. Includes (1) PM (7x24) to be performed at beginning of year three. Must be purchased concurrently with equipment. Zone 1 - within 100 miles of XPC Service Center. | 9300
90001251 | X902S1YREE | X90 One-year extension of factory on-site warranty, electronics only. This warranty covers parts and labor, extending standard factory warranty by 1yr. Includes (1) PM (7x24) to be performed at beginning of the extension year. Maximum of 5 years. | 8800
90001252 | X902SPM7 | X90-2S Preventative Maintenance Service, 7x24. For Zone 1 (within 100 miles of XPC Service Center). | 5800
90000538 | SVCADD | Service adder for locations further than 100 miles. | 1200

## XPDU & SPDU
|  | Return to Index | 2025-11-01
SPDU SERIES
Switched and Metered PDU
Part Number | Model | Description | List Price
90001340 | SPDU-0615C | Xtreme Power Switched and Metered-by-Outlet Power Distribution Unit (SPDU) with C14 power inlet and detachable 6-ft 5-15P to C13 power cord; (6) NEMA 5-15R outlets, each individually monitored and remotely controlled via integrated SNMP network interface and management software; Front-panel LCD displays outlet status, load, and temperature data. Includes 1080 J surge protection and built-in temperature sensor. 5-Year Warranty (USA & Canada). Certifications: UL 62368-1, CSA C22.2 No. 62368-1, UL 1449 Ed. 5, FCC Class B, TAA Compliant; 17.3″ W × 2.8″ D × 1.73″ H, 2.3 lbs. | 725
90001341 | SPDU-1415C | Xtreme Power Switched and Metered-by-Outlet Power Distribution Unit (SPDU) with C14 power inlet and detachable 6-ft 5-15P to C13 power cord; (14) NEMA 5-15R outlets, each individually monitored and remotely controlled via integrated SNMP network interface and management software; Front-panel LCD displays outlet status, load, and temperature data. Includes 3240 J surge protection and built-in temperature sensor. 5-Year Warranty (USA & Canada). Certifications: UL 62368-1, CSA C22.2 No. 62368-1, UL 1449 Ed. 5, FCC Class B, TAA Compliant; 17.3″ W × 3.5″ D × 3.5″ H, 5.4 lbs. | 950
XPDU SERIES
Switched PDU
Part Number | Model | Description | List Price
90000460 | SPD-0215 | Xtreme Power XPDU Series Switched Power PDU with C14 Power inlet with removeable 5-15P to C13 power cord; (2) 5-15/20R output receptacles each independently power controlled via included SNMP Port and Software; 2-Year Warranty; 6"W x 6.8"D x 1.9"H, 2.0 lbs | 519
90000765 | J40SP | Xtreme Power XPDU Series, Ultra Slim Switched Power PDU with IEC-C14 Inlet (optional line cords available). (3) 5-15R output receptacles each independently power controlled via included RJ45 SNMP Port and Software; Pass through RJ45 Port enables connection of additional network devices; Easy to read LED display shows on/off condition of individual receptacles; 3-Year Warranty; 8.07W"W x 7.28"D x 1.22"H, 3.25 lbs | 549
| XPC-515P-3RA | Optional 3 ft, 5-15P line cord with right angle offset for use with J40 series PDU. .5 lbs | 22
| XPC-515P-6RA | Optional 6ft, 5-15P line cord with right angle offset for use with J40 series PDU. .5 lbs | 22
Transformer PDU
Part Number | Model | Description | List Price
900007742 | JX-200 | J60 200W Isolation Transformer, 120 VAC, 50/60Hz, C14 inlet with removeable 5-15P line cord; (3) 5-15R output receptacles; 5A output breaker; complete line isolation; Common Mode and Normal Mode noise filtering; 300 joules surge suppression; UL16950, RoHS; 5-Year Full Warranty; 6.9" W x 8.5" D x 1.25" H; 6.6 lbs. | 220
90000739 | XPD-IT15A | Xtreme Power XPDU Series PDU with Isolation Transformer. 1500W, 208V in, 120V out. IEC-C14 inlet with 3' 5-15 line cord ; (16) 5-15R output receptacles protected by 15A breaker; 3-Year Warranty; 17.5"W x 15"D x 3.5"H (2U), 43 lbs. | 980
90000407 | XPD-IT60A | Xtreme Power XPDU Series 6KVA PDU with Isolation Transformer for use with P80G-5000 or P91 5-10K UPS. 6000W, 208 or 240 in, 208/104V or 240/120V out. 3ft L6-30P Input Cord. (1) L6-30R and (12) 5-15-20R output receptacles; rear panel 208/240 voltage selection switch; includes front panel rackmount brackets; ROHS Approved; 3-Year Warranty; 17.3"W x 18"D x 3.5"H (2U), 137 lbs. | 1750
90000781 | XPD-IT6KW | 6kVA PDU with Isolation Transformer 208V to 240/120V (or 240V to 240/120V), Input terminal bock, Output terminal block + (2) L14-30R and (8) 5–15/20R receptacles; 17.3”W x 31.8”D x 5.2”H; 122 lbs. | 2310
90000740 | XPD-IT10KW | 10kVA PDU with Isolation Transformer 208V to 240/120V (or 240V to 240/120V), Input terminal bock, Output terminal block + (2) L14-30R and (8) 5–15/20R receptacles; 17.3”W x 31.8”D x 5.2”H; 122 lbs. | 2760
Basic PDU 10A Models
Part Number | Model | Description | List Price
90000463 | J40 | Xtreme Power XPDU; ultra slim 120VAC, 10 Amp PDU with IEC-C14 Inlet (optional line cords available). (3) 5-15R output receptacles; Power reset button for manual recycling of power. 2400 Joules surge protection; 3-Year Warranty; 8.07W"W x 3.35"D x 1.22"H, 2 lbs | 210
90000466 | J40i | Xtreme Power XPDU; ultra slim 230 VAC, 10 Amp PDU with IEC-C14 Inlet (optional line cords available). (3) IEC C13 output receptacles; Power reset button for manual recycling of power. 2400 Joules surge protection; 3-Year Warranty; 8.07W"W x 3.35"D x 1.22"H, 2 lbs | 210
| XPC-515P-3RA | Optional 3 ft, 5-15P line cord with right angle offset for use with J40 series PDU. .5 lbs | 22
| XPC-515P-6RA | Optional 6ft, 5-15P line cord with right angle offset for use with J40 series PDU. .5 lbs | 22
Basic PDU 15A & 20A Models
Part Number | Model | Description | List Price
90000040 | XPD815HV | Xtreme Power XPDU Series Basic Power PDU with 12' Input line cord with 5-15P plug; (8) 5-15R output receptacles on rear of PDU; UL60950-1/cUL/FCC Approved; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 2.6 lbs | 120
90000041 | XPD1415HV | Xtreme Power XPDU Series Basic Power PDU with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of PDU + (8) 5-15R output receptacles on rear of PDU; UL60950-1/cUL/FCC Approved; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 3.5 lbs | 138
90000045 | XPD1420HV | Xtreme Power XPDU Series Basic Power PDU with 12' Input line cord with L5-20P plug (L5-20 to 5-20 adapter included); (6) 5-20R output receptacles on front of PDU + (8) 5-20R output receptacles on rear of PDU; UL60950-1/cUL/FCC Approved; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 4.8 lbs | 190
90000046 | XPD2420V60 | Xtreme Power XPDU Series Basic Power PDU with 12' Input line cord with L5-20P plug (L5-20 to 5-20 adapter included); (24) 5-20R output receptacles; vertical mounting only; UL60950-1/cUL/FCC Approved; 3-Year Warranty; 60"W x 1.5"D x 1.5"H, 5.6 lbs * | 182
90000053 | XPDU-IEC | Xtreme Power XPDU Series Basic Power 230V PDU with C20 inlet (power cord ordered separately), (10) IEC C13 + (2) IEC C19 output receptacles; 1U Rackmount configuration; CE Listed; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 2.6 lbs | 190
Basic PDU - 30A & 50A Models
Part Number | Model | Description | List Price
90000374 | XPD24C13V | Xtreme Power XPDU Series Basic Power PDU, 30A, 200-240V; L6-30P 6ft line cord, (24) C13 output receptacles. Vertical Mount. 1.75"W x 1.75"D x 66"L. 12 lbs | 340
90000251 | XPD31 | Xtreme Power XPDU Series Basic Power PDU, 30A, 200-240V; L6-30P 6ft line cord, (2) L6-30R, (2) L6-20R and (4) 6-15/20R output receptacles. Rackmount. 19"W x 4.7"D x 3.5"H. 9 lbs | 580
90000252 | XPD32 | Xtreme Power XPDU Series Basic Power PDU, 30A, 200-240V; L6-30P 6ft line cord, (2) L6-30R, (4) L6-20R output receptacles. Rackmount. 19"W x 2.4"D x 3.5"H. 7.5 lbs | 580
90000253 | XPD33 | Xtreme Power XPDU Series Basic Power PDU, 30A, 200-240V; L6-30P 6ft line cord, (4) IEC-C19 and (8) IEC C13 output receptacle. s Rackmount. 19"W x 2.4"D x 3.5"H. 8 lbs | 450
90000254 | XPD34 | Xtreme Power XPDU Series Basic Power PDU, 30A, 240/120V; L14-30P 6ft line cord, (2) L6-30R, (4) L6-20R and (12) 5-20R output receptacles. Rackmount. 19"W x 4.7"D x 3.5"H. 9.5 lbs | 690
90000255 | XPD35 | Xtreme Power XPDU Series Basic Power PDU, 50A, 200-240V; Hardwire input with Pigtail, (2) L6-30R and (4) L6-20R output receptacles. Rackmount. 19"W x 2.4"D x 3.5"H. 7 lbs | 580
90000256 | XPD36 | Xtreme Power XPDU Series Basic Power PDU, 50A, 200-240V; Hardwired input with Pigtail, (4) IEC-C19 and (8) IEC C13 output receptacles. Rackmount. 19"W x 2.4"D x 3.5"H. 6.8 lbs | 460
90000257 | XPD37 | Xtreme Power XPDU Series Basic Power PDU, 50A, 240/120V; Hardwired input with Pigtail, (2) L6-30R, (4) L6-20R and (12) 5-20R output receptacles. Rackmount. 19"W x 4.7"D x 3.5"H. 10 lbs | 690
90001037 | XPD38 | Xtreme Power XPDU Series Basic Power PDU, 30A, 120V; L14-30P, 6' input cord , (4) L5-30R, (4) L5-20R output receptacles. Rackmount. 19"W x 4.7"D x 3.5"H. 9.5 lbs | 690
90001038 | XPD39 | Xtreme Power XPDU Series Basic Power PDU, 50A, 120V; hardwire input with pigtail, (4) L5-30R, (4) L5-20R output receptacles. Rackmount. 19"W x 4.7"D x 3.5"H. 9.5 lbs | 690
Surge PDU
Part Number | Model | Description | List Price
90000048 | XPDS1015HV | Xtreme Power XPDU Series Surge Power PDU with 12' Input line cord with5-15P plug; (2) 5-15R surge protected output receptacles on front of PDU + (8) 5-15R surge protected output receptacles on rear of PDU; 342 Joule Rating; UL60950-1/cUL/FCC Approved; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 4.4 lbs * | 159
90000049 | XPDS1020HV | Xtreme Power XPDU Series Surge Power PDU with 12' Input line cord with L5-20P plug (L5-20 to 5-20 adapter included); (2) 5-15/20R surge protected output receptacles on front of PDU + (8) 5-15/20R surge protected output receptacles on rear of PDU; 342 Joule Rating; UL60950-1/cUL/FCC Approved; 3-Year Warranty; 19"W x 3.5"D x 1.75"H, 4.6 lbs * | 179
Value PDU
Part Number | Model | Description | List Price
90000051 | XPD1215HVPL | Xtreme Power XPDU Series Value Power PDU with 6' Input line cord with 5-15P plug; (12) 5-15R output receptacles; Plastic case; UL60950-1/cUL/FCC Approved; 3-Year Warranty; 19.0"W x 1.5"D x 1.75"H, 1.4 lbs * | 58

## XBDM
|  | Return to Index | 2024-08-01
XBDM SERIES
Part Number | Model | Description | List Price
90000090 | XBDM-1015LV | Xtreme Power XBDM Series 15 Amp Maintenance Bypass Distribution Module with 12' Input line cord with 5-15P plug; (6) 5-15R output receptacles on front of BDM + (4) 5-15R output receptacles on rear of BDM; bypass switch allows for maintenance of the UPS without affecting the load connected; 3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 379
90000091 | XBDM-1020LV | Xtreme Power XBDM Series20 Amp Maintenance Bypass Distribution Module with 12' Input line cord with 5-20P plug; (6) 5-20R output receptacles on front of BDM + (4) 5-20R output receptacles on rear of BDM; bypass switch allows for maintenance of the UPS without affecting the load connected; 3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 419
90000093 | XBDM-1030LV | Xtreme Power XBDM Series30 Amp Maintenance Bypass Distribution Module with 6' Input line cord with L5-30P plug; (5) 5-20R output receptacles on front of BDM (Load Group 1) + (5) 5-20R output receptacles on rear of BDM (Load Group 2); (2) bypass switches allow for maintenance of the UPS without affecting the loads connected; 3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 659
90000095 | XBDM1020HV1 | Xtreme Power XBDM Series Maintenance Bypass Distribution Module with C20 inlet for customer supplied power cord; rated at 16A; (2) IEC C19 and (4) IEC C13 output receptacles on front + (4) IEC C13 output receptacles on back; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads; Includes IEC C20 to C13 cord kit for connecting the XBDM to a T90i-1500, NXRTi-1000 or G90-1000 UPS; 3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 369
90000094 | XBDM1020HV2 | Xtreme Power XBDM Series Maintenance Bypass Distribution Module with C20 inlet for customer supplied power cord; rated at 16A; (2) IEC C19 and (4) IEC C13 output receptacles on front + (4) IEC C13 output receptacles on back; Includes maint bypass switch allowing for bypassing and maintenance of the UPS without affecting the connected loads; Includes (2) IEC C20 to C19 cord kits for connecting the XBDM to the P90G-3000 or P90LG-3000 UPS; 3-Year Warranty (USA only); 19"W x 3.5"D x 1.75"H, 3.5 lbs | 419
90000949 | XBDM-15RHW | Xtreme Power XBDM Series 15 Amp Maintenance Bypass Distribution Module with HW terminal block input; output is HW terminal block and (6) 5-15/20R receptacles; Cnnection to UPS is 5-15P (3ft) and 5-20R; Rackmountable; Allows fo rbypassing and maintenance of the UPS without affecting the loads connected; 3-Year Warranty (USA only); 17"W x 3.5"D x 1.75"H, 3.6 lbs | 369
90000950 | XBDM-20RHW | Xtreme Power XBDM Series 20 Amp Maintenance Bypass Distribution Module with HW terminal block input; output is HW terminal block and (6) 5-15/20R receptacles; Connection to UPS is 5-20P (3ft) and 5-20R; Rackmountable; Allows fo rbypassing and maintenance of the UPS without affecting the loads connected; 3-Year Warranty (USA only); 17"W x 3.5"D x 1.75"H, 3.6 lbs | 369
90000947 | XBDM-HW30 | Xtreme Power XBDM Series 30 Amp Maintenance Bypass Distribution Module; Hardwired input and output terminal block connection; Connection to UPS is via L5-30R receptacle and 3' power cord with L5-30P plug; Rackmountable; Includes rotary bypass switch, allowing for bypass and maintenance of the UPS without affecting the connected loads; 3-Year Warranty (USA only); 17.25"W x 5.25"D x 3.5"H, 7.3 lbs | 620
90000934 | XBDM-HW63 | Xtreme Power XBDM Series 208VAC, 63 Amp Maintenance Bypass Distribution Module; Hardwire or optional cable kit input, Hardwire terminal block output; Connects to UPS via Hardwire or optional cable kit; Make-Before-Break; includes an inverter interlock; Rackmountable; Allows for maintenance of the UPS without affecting the loads connected; Interconnect cables supplied by others; 3-Year Warranty (USA only); 17.25"W x 5.25"D x 3.5"H, 7.1 lbs | 570

## Battery
|  | Return to Index | 2024-08-01
Replacement Batteries and Battery Packs
Individual Replacement Batteries
Part Number | Model Number | Description | List Price
| HRL1234WF2 | 12V, 9AH Rechargeable sealed Lead Acid AGM Maintenance Free replacement battery. _____ UPS requires (_) batteries. F2 (.25 inch) faston tabs. One Year Warranty. 2.6"W x 5.9"L x 3.9"H. 6 lbs. | 59
| UPS12580 | 12V, 580Watt Rechargeable sealed Lead Acid AGM Maintenance Free replacement battery. _____ UPS requires (_) batteries. F2 (.25 inch) faston tabs. One Year Warranty. 2.6"W x 5.9"L x 9.9"H. 5 lbs. | 65
Replacement Battery Packs
Part Number | Model Number | Description | List Price
90000549 | J60-BAT1 | Replacement battery pack for J60-350 UPS (1) Required per UPS. Includes LiFePo4 batteries and Protection Circuit Module (PCM). One Year Warranty. 2.6"W x 5.0"L x 1.0"H. | 195
90001046 | J60-BAT2 | Replacement battery pack for J60-600 UPS (1) Required per UPS. Includes LiFePo4 batteries and Protection Circuit Module (PCM). One Year Warranty. 2.6"W x 5.0"L x 1.0"H. | 432
90000478 | P80-BAT580 | Replacement battery pack for P80g-5000 UPS, and P80-BP72X. (1) Required per UPS and (2) Required per BP.. One Year Warranty. 8.5"W x 18.5"L x 2.6"H. 37 lbs | 495
90000370 | P90-BAT1 | Replacement battery pack for P90-1000, P80-800 and P80-1100 UPS. (1) Required per UPS. One Year Warranty. 6.5"W x 8.0"L x 2.6"H. 13 lbs. | 245
90000371 | P90-BAT2 | Replacement battery pack for P90-1500 UPS or P90-BP36. (1) Required per UPS, (2) required per P90-BP36. One Year Warranty. 8.5"W x 12.6"L x 2.6"H. 19 lbs. | 295
90000372 | P90-BAT3 | Replacement battery pack for P90-2000, P80-1500, P80-2000 UPS or P90-BP48. (1) Required per UPS, (2) required per P90-BP48. One Year Warranty. 8.5"W x 12.6"L x 2.6"H. 25 lbs. | 350
90000373 | P90-BAT4 | Replacement battery pack for P90-3000, P90G-3000, P80-2200, P80-3000, P80G-3000 UPS or P90-BP72. (1) Required per UPS, (2) required per B90-BP72. One Year Warranty. 8.5"W x 18.5"L x 2.6"H. 37 lbs. | 465